## overview
Start with gas phase fuel (CH4 or H2) and 15% excess air (N2 and O2) at 25’C and 1bar
End with the CO2, H2O, O2, and N2 products at a constant flue gas temperature and 1 bar
But what flue gas temperature do we use?
Bases on https://www.heatgeek.com/condensing-boilers-efficiency/
(Which is itself referencing https://www.ashrae.org/about/news/2016/ashrae-2016-handbook-focuses-on-hvac-systems-and-equipment)
56.02'C is the flue gas dew point temperature (H2O vapour pressure of 0.1667 bar))
To get condensation, need flue gas temperature below this
Amount of condensation is non-linear, as dew point changes as dew condenses out
at 50'C the vapour pressure of H2O is 0.1265 bar
corresponds to about 27% of the H2O having condensed out of the gas phase
THEREFORE the outlet conditions of a condensing boiler is 50'C flue gas and 27% condensation
Higher Heating Value (HHV) has a specific meaning:
bringing all the products down to pre-combustion temperature, and condensing all vapour
Lower Heating Value (LHV) has no aggreed on meaning, but most commonly it is HHV - vaporisation of H2O
CH4 properties
https://webbook.nist.gov/cgi/cbook.cgi?ID=C74828&Mask=1
the rest I just took from Wolfram Alpha

## vapour pressure
T [C] | Partial [%]
0 | 0.006 | https://en.wikipedia.org/wiki/Vapour_pressure_of_water
5 | 0.0086
10 | 0.0121
15 | 0.0168
20 | 0.0231
25 | 0.0313
30 | 0.0419
35 | 0.0555
40 | 0.0728
45 | 0.0946
50 | 0.1218
51 | 0.12808 | https://www.spiraxsarco.com/resources-and-design-tools/steam-tables/saturated-water-line#article-top
52 | 0.13453
53 | 0.14125
54 | 0.14826
55 | 0.15556
55.5837 | 0.16 | interpolated, dew point of CH4
56 | 0.16317
57 | 0.17109
58 | 0.17934
59 | 0.18792
60 | 0.19686
61 | 0.20615
62 | 0.21581
63 | 0.22586
64 | 0.2363
65 | 0.24714
66 | 0.25841
67 | 0.27011
68 | 0.28225
69 | 0.29485
69.1107 | 0.2963 | interpolated, dew point of H2
70 | 0.30793
71 | 0.32149
72 | 0.33556
73 | 0.35014
74 | 0.36525
75 | 0.38091
76 | 0.39713
77 | 0.41392
78 | 0.43132
79 | 0.44932
80 | 0.46794
81 | 0.48722
82 | 0.50715
83 | 0.52777
84 | 0.54908
85 | 0.5711
86 | 0.59386
87 | 0.61738
88 | 0.64167
89 | 0.66675
90 | 0.69264
91 | 0.71937
92 | 0.74695
93 | 0.7754
94 | 0.80475
95 | 0.83502
96 | 0.86623
97 | 0.8984
98 | 0.93156
99 | 0.96572
100 | 1

## CH4 overview
CH4 reaction
CH4 + 2 O2 > CO2 + 2 H2O
|  | CH4 | O2 | N2 | CO2 | H2O
fuel | mol | 1
air | mol |  | 2.3 | 9.2
products | mol |  | 0.3 | 9.2 | 1 | 2
product fraction | % |  | 2.4% | 73.6% | 8% | 16%
products | mol |  | 0.3 | 9.2 | 1 | 1.4563
product fraction | % |  | 2.509% | 76.95% | 8.364% | 12.18%
[5 empty] | condensed | 0.27186
HHV | kJ/mol | 890.7
average HHV | kJ/mol | 890.7
Heat capacity | J/mol/K | 34.92 | 29.4 | 29.13 | 37.1 | 74.88
heat of vaporiation | kJ/mol |  |  |  |  | 40.2
inlet temperature | C | 25
outlet temperature | C | 50
non condensed | % | 72.81%
sensible heat | kJ/mol | 0 | 0.2205 | 6.6999 | 0.9275 | 3.744 | 11.5919
latent heat | kJ/mol |  |  |  |  | 58.5422
total heat | kJ/mol(rxn) | 70.1341
Effective Heating Value | kJ/mol(rxn) | 820.5659 | 92.13%

## CH4 eff
Inlet [C] | Combustion [kJ/mol] | Outlet [C] | Partial Pressure | Methane | O2 mol | N2 mol | CO2 mol | H2O mol | H2O left | O2 Cp | N2 Cp | CO2 Cp | H2O Cp | H2O vap | O2 sensible | N2 sensible | CO2 sensible | H2O sensible | H2O latent | total heat
25 | 890.7 | 0 | 0.006 | 101% | 0.3 | 9.2 | 1 | 2 | 0.06338 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.2205 | -6.6999 | -0.9275 | -3.744 | 2.5479 | -9.044
25 | 890.7 | 5 | 0.0086 | 100.6% | 0.3 | 9.2 | 1 | 2 | 0.091083 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.1764 | -5.3599 | -0.742 | -2.9952 | 3.6615 | -5.612
25 | 890.7 | 10 | 0.0121 | 100.2% | 0.3 | 9.2 | 1 | 2 | 0.12861 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.1323 | -4.0199 | -0.5565 | -2.2464 | 5.17 | -1.7852
25 | 890.7 | 15 | 0.0168 | 99.71% | 0.3 | 9.2 | 1 | 2 | 0.17941 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.0882 | -2.68 | -0.371 | -1.4976 | 7.2124 | 2.5757
25 | 890.7 | 20 | 0.0231 | 99.14% | 0.3 | 9.2 | 1 | 2 | 0.24829 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.0441 | -1.34 | -0.1855 | -0.7488 | 9.9811 | 7.6627
25 | 890.7 | 25 | 0.0313 | 98.47% | 0.3 | 9.2 | 1 | 2 | 0.33927 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0 | 0 | 0 | 0 | 13.6386 | 13.6386
25 | 890.7 | 30 | 0.0419 | 97.67% | 0.3 | 9.2 | 1 | 2 | 0.45919 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.0441 | 1.34 | 0.1855 | 0.7488 | 18.4594 | 20.7778
25 | 890.7 | 35 | 0.0555 | 96.69% | 0.3 | 9.2 | 1 | 2 | 0.61699 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.0882 | 2.68 | 0.371 | 1.4976 | 24.8031 | 29.4399
25 | 890.7 | 40 | 0.0728 | 95.5% | 0.3 | 9.2 | 1 | 2 | 0.82442 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.1323 | 4.0199 | 0.5565 | 2.2464 | 33.1416 | 40.0967
25 | 890.7 | 45 | 0.0946 | 94.01% | 0.3 | 9.2 | 1 | 2 | 1.0971 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.1764 | 5.3599 | 0.742 | 2.9952 | 44.1028 | 53.3763
25 | 890.7 | 50 | 0.1218 | 92.13% | 0.3 | 9.2 | 1 | 2 | 1.4563 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2205 | 6.6999 | 0.9275 | 3.744 | 58.5422 | 70.1341
25 | 890.7 | 51 | 0.12808 | 91.68% | 0.3 | 9.2 | 1 | 2 | 1.5424 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.22932 | 6.9679 | 0.9646 | 3.8938 | 62.0063 | 74.0618
25 | 890.7 | 52 | 0.13453 | 91.23% | 0.3 | 9.2 | 1 | 2 | 1.6321 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.23814 | 7.2359 | 1.0017 | 4.0435 | 65.6113 | 78.1306
25 | 890.7 | 53 | 0.14125 | 90.75% | 0.3 | 9.2 | 1 | 2 | 1.7271 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.24696 | 7.5039 | 1.0388 | 4.1933 | 69.429 | 82.4119
25 | 890.7 | 54 | 0.14826 | 90.24% | 0.3 | 9.2 | 1 | 2 | 1.8277 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.25578 | 7.7719 | 1.0759 | 4.343 | 73.4726 | 86.9192
25 | 890.7 | 55 | 0.15556 | 89.71% | 0.3 | 9.2 | 1 | 2 | 1.9343 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2646 | 8.0399 | 1.113 | 4.4928 | 77.7579 | 91.6682
25 | 890.7 | 55.5837 | 0.16 | 89.38% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.26975 | 8.1963 | 1.1347 | 4.5802 | 80.4 | 94.5809
25 | 890.7 | 56 | 0.16317 | 89.36% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.27342 | 8.3079 | 1.1501 | 4.6426 | 80.4 | 94.774
25 | 890.7 | 57 | 0.17109 | 89.31% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.28224 | 8.5759 | 1.1872 | 4.7923 | 80.4 | 95.2376
25 | 890.7 | 58 | 0.17934 | 89.26% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.29106 | 8.8439 | 1.2243 | 4.9421 | 80.4 | 95.7013
25 | 890.7 | 59 | 0.18792 | 89.2% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.29988 | 9.1119 | 1.2614 | 5.0918 | 80.4 | 96.165
25 | 890.7 | 60 | 0.19686 | 89.15% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.3087 | 9.3799 | 1.2985 | 5.2416 | 80.4 | 96.6287
25 | 890.7 | 61 | 0.20615 | 89.1% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.31752 | 9.6479 | 1.3356 | 5.3914 | 80.4 | 97.0923
25 | 890.7 | 62 | 0.21581 | 89.05% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.32634 | 9.9159 | 1.3727 | 5.5411 | 80.4 | 97.556
25 | 890.7 | 63 | 0.22586 | 89% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.33516 | 10.1838 | 1.4098 | 5.6909 | 80.4 | 98.0197
25 | 890.7 | 64 | 0.2363 | 88.94% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.34398 | 10.4518 | 1.4469 | 5.8406 | 80.4 | 98.4834
25 | 890.7 | 65 | 0.24714 | 88.89% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.3528 | 10.7198 | 1.484 | 5.9904 | 80.4 | 98.947
25 | 890.7 | 66 | 0.25841 | 88.84% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.36162 | 10.9878 | 1.5211 | 6.1402 | 80.4 | 99.4107
25 | 890.7 | 67 | 0.27011 | 88.79% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.37044 | 11.2558 | 1.5582 | 6.2899 | 80.4 | 99.8744
25 | 890.7 | 68 | 0.28225 | 88.73% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.37926 | 11.5238 | 1.5953 | 6.4397 | 80.4 | 100.3381
25 | 890.7 | 69 | 0.29485 | 88.68% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.38808 | 11.7918 | 1.6324 | 6.5894 | 80.4 | 100.8017
25 | 890.7 | 69.1107 | 0.2963 | 88.68% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.38906 | 11.8215 | 1.6365 | 6.606 | 80.4 | 100.8531
25 | 890.7 | 70 | 0.30793 | 88.63% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.3969 | 12.0598 | 1.6695 | 6.7392 | 80.4 | 101.2654
25 | 890.7 | 71 | 0.32149 | 88.58% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.40572 | 12.3278 | 1.7066 | 6.889 | 80.4 | 101.7291
25 | 890.7 | 72 | 0.33556 | 88.53% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.41454 | 12.5958 | 1.7437 | 7.0387 | 80.4 | 102.1928
25 | 890.7 | 73 | 0.35014 | 88.47% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.42336 | 12.8638 | 1.7808 | 7.1885 | 80.4 | 102.6564
25 | 890.7 | 74 | 0.36525 | 88.42% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.43218 | 13.1318 | 1.8179 | 7.3382 | 80.4 | 103.1201
25 | 890.7 | 75 | 0.38091 | 88.37% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.441 | 13.3998 | 1.855 | 7.488 | 80.4 | 103.5838
25 | 890.7 | 76 | 0.39713 | 88.32% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44982 | 13.6678 | 1.8921 | 7.6378 | 80.4 | 104.0475
25 | 890.7 | 77 | 0.41392 | 88.27% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.45864 | 13.9358 | 1.9292 | 7.7875 | 80.4 | 104.5112
25 | 890.7 | 78 | 0.43132 | 88.21% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.46746 | 14.2038 | 1.9663 | 7.9373 | 80.4 | 104.9748
25 | 890.7 | 79 | 0.44932 | 88.16% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.47628 | 14.4718 | 2.0034 | 8.087 | 80.4 | 105.4385
25 | 890.7 | 80 | 0.46794 | 88.11% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.4851 | 14.7398 | 2.0405 | 8.2368 | 80.4 | 105.9022
25 | 890.7 | 81 | 0.48722 | 88.06% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.49392 | 15.0078 | 2.0776 | 8.3866 | 80.4 | 106.3659
25 | 890.7 | 82 | 0.50715 | 88.01% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.50274 | 15.2758 | 2.1147 | 8.5363 | 80.4 | 106.8295
25 | 890.7 | 83 | 0.52777 | 87.95% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.51156 | 15.5438 | 2.1518 | 8.6861 | 80.4 | 107.2932
25 | 890.7 | 84 | 0.54908 | 87.9% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.52038 | 15.8118 | 2.1889 | 8.8358 | 80.4 | 107.7569
25 | 890.7 | 85 | 0.5711 | 87.85% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5292 | 16.0798 | 2.226 | 8.9856 | 80.4 | 108.2206
25 | 890.7 | 86 | 0.59386 | 87.8% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.53802 | 16.3478 | 2.2631 | 9.1354 | 80.4 | 108.6842
25 | 890.7 | 87 | 0.61738 | 87.75% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.54684 | 16.6158 | 2.3002 | 9.2851 | 80.4 | 109.1479
25 | 890.7 | 88 | 0.64167 | 87.69% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.55566 | 16.8837 | 2.3373 | 9.4349 | 80.4 | 109.6116
25 | 890.7 | 89 | 0.66675 | 87.64% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.56448 | 17.1517 | 2.3744 | 9.5846 | 80.4 | 110.0753
25 | 890.7 | 90 | 0.69264 | 87.59% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5733 | 17.4197 | 2.4115 | 9.7344 | 80.4 | 110.5389
25 | 890.7 | 91 | 0.71937 | 87.54% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.58212 | 17.6877 | 2.4486 | 9.8842 | 80.4 | 111.0026
25 | 890.7 | 92 | 0.74695 | 87.49% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.59094 | 17.9557 | 2.4857 | 10.0339 | 80.4 | 111.4663
25 | 890.7 | 93 | 0.7754 | 87.43% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.59976 | 18.2237 | 2.5228 | 10.1837 | 80.4 | 111.93
25 | 890.7 | 94 | 0.80475 | 87.38% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.60858 | 18.4917 | 2.5599 | 10.3334 | 80.4 | 112.3936
25 | 890.7 | 95 | 0.83502 | 87.33% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.6174 | 18.7597 | 2.597 | 10.4832 | 80.4 | 112.8573
25 | 890.7 | 96 | 0.86623 | 87.28% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.62622 | 19.0277 | 2.6341 | 10.633 | 80.4 | 113.321
25 | 890.7 | 97 | 0.8984 | 87.23% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.63504 | 19.2957 | 2.6712 | 10.7827 | 80.4 | 113.7847
25 | 890.7 | 98 | 0.93156 | 87.17% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.64386 | 19.5637 | 2.7083 | 10.9325 | 80.4 | 114.2483
25 | 890.7 | 99 | 0.96572 | 87.12% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.65268 | 19.8317 | 2.7454 | 11.0822 | 80.4 | 114.712
25 | 890.7 | 100 | 1 | 87.07% | 0.3 | 9.2 | 1 | 2 | 2 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.6615 | 20.0997 | 2.7825 | 11.232 | 80.4 | 115.1757

## H2 overview
H2 reaction
H2 + 0.5 O2 > H2O
|  | H2 | O2 | N2 | H2O
fuel | mol | 1
air |  |  | 0.575 | 2.3
products | mol |  | 0.075 | 2.3 | 1
product fraction | % |  | 2.222% | 68.15% | 29.63%
products | mol |  | 0.075 | 2.3 | 0.3294
product fraction | % |  | 2.773% | 85.05% | 12.18%
|  |  |  | condensed | 0.6706
HHV | kJ/mol | 285.8
average HHV | kJ/mol | 285.8
Heat capacity | J/mol/K | 28.83 | 29.4 | 29.13 | 74.88
heat of vaporiation | kJ/mol |  |  |  | 40.2
inlet temperature | C | 25
outlet temperature | C | 50
non condensed | % | 32.94%
sensible heat | kJ/mol | 0 | 0.055125 | 1.675 | 1.872 | 3.6021
latent heat | kJ/mol |  |  |  | 13.2417
total heat | kJ/mol(rxn) | 16.8438
Effective Heating Value | kJ/mol(rxn) | 268.9562 | 94.11%

## H2 eff
Inlet [C] | Combustion [kJ/mol] | Outlet [C] | Partial Pressure | Hydrogen | O2 mol | N2 mol | H2O mol | H2O left | O2 Cp | N2 Cp | H2O Cp | H2O vap | O2 sensible | N2 sensible | H2O sensible | H2O latent | total heat
25 | 285.8 | 0 | 0.006 | 101.1% | 0.075 | 2.3 | 1 | 0.014336 | 0.0294 | 0.02913 | 0.07488 | 40.2 | -0.055125 | -1.675 | -1.872 | 0.57631 | -3.0258
25 | 283.8 | 5 | 0.0086 | 100.7% | 0.075 | 2.3 | 1 | 0.020602 | 0.0294 | 0.02913 | 0.07488 | 40.2 | -0.0441 | -1.34 | -1.4976 | 0.82821 | -2.0535
25 | 283.8 | 10 | 0.0121 | 100.3% | 0.075 | 2.3 | 1 | 0.029089 | 0.0294 | 0.02913 | 0.07488 | 40.2 | -0.033075 | -1.005 | -1.1232 | 1.1694 | -0.99186
25 | 283.8 | 15 | 0.0168 | 99.93% | 0.075 | 2.3 | 1 | 0.040582 | 0.0294 | 0.02913 | 0.07488 | 40.2 | -0.02205 | -0.66999 | -0.7488 | 1.6314 | 0.19055
25 | 283.8 | 20 | 0.0231 | 99.46% | 0.075 | 2.3 | 1 | 0.05616 | 0.0294 | 0.02913 | 0.07488 | 40.2 | -0.011025 | -0.33499 | -0.3744 | 2.2576 | 1.5372
25 | 283.8 | 25 | 0.0313 | 98.91% | 0.075 | 2.3 | 1 | 0.076739 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0 | 0 | 0 | 3.0849 | 3.0849
25 | 283.8 | 30 | 0.0419 | 98.27% | 0.075 | 2.3 | 1 | 0.10386 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.011025 | 0.33499 | 0.3744 | 4.1753 | 4.8958
25 | 283.8 | 35 | 0.0555 | 97.52% | 0.075 | 2.3 | 1 | 0.13956 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.02205 | 0.66999 | 0.7488 | 5.6102 | 7.0511
25 | 283.8 | 40 | 0.0728 | 96.6% | 0.075 | 2.3 | 1 | 0.18648 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.033075 | 1.005 | 1.1232 | 7.4963 | 9.6576
25 | 283.8 | 45 | 0.0946 | 95.47% | 0.075 | 2.3 | 1 | 0.24815 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.0441 | 1.34 | 1.4976 | 9.9756 | 12.8573
25 | 283.8 | 50 | 0.1218 | 94.06% | 0.075 | 2.3 | 1 | 0.3294 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.055125 | 1.675 | 1.872 | 13.2417 | 16.8438
25 | 283.8 | 51 | 0.12808 | 93.74% | 0.075 | 2.3 | 1 | 0.34889 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.05733 | 1.742 | 1.9469 | 14.0252 | 17.7714
25 | 283.8 | 52 | 0.13453 | 93.4% | 0.075 | 2.3 | 1 | 0.36917 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.059535 | 1.809 | 2.0218 | 14.8407 | 18.7309
25 | 283.8 | 53 | 0.14125 | 93.04% | 0.075 | 2.3 | 1 | 0.39065 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.06174 | 1.876 | 2.0966 | 15.7042 | 19.7385
25 | 283.8 | 54 | 0.14826 | 92.67% | 0.075 | 2.3 | 1 | 0.4134 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.063945 | 1.943 | 2.1715 | 16.6188 | 20.7972
25 | 283.8 | 55 | 0.15556 | 92.28% | 0.075 | 2.3 | 1 | 0.43751 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.06615 | 2.01 | 2.2464 | 17.5881 | 21.9106
25 | 283.8 | 55.5837 | 0.16 | 92.04% | 0.075 | 2.3 | 1 | 0.45238 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.067437 | 2.0491 | 2.2901 | 18.1857 | 22.5923
25 | 283.8 | 56 | 0.16317 | 91.87% | 0.075 | 2.3 | 1 | 0.46308 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.068355 | 2.077 | 2.3213 | 18.6159 | 23.0825
25 | 283.8 | 57 | 0.17109 | 91.43% | 0.075 | 2.3 | 1 | 0.49021 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.07056 | 2.144 | 2.3962 | 19.7062 | 24.3169
25 | 283.8 | 58 | 0.17934 | 90.97% | 0.075 | 2.3 | 1 | 0.51901 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.072765 | 2.211 | 2.471 | 20.864 | 25.6188
25 | 283.8 | 59 | 0.18792 | 90.49% | 0.075 | 2.3 | 1 | 0.5496 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.07497 | 2.278 | 2.5459 | 22.0939 | 26.9928
25 | 283.8 | 60 | 0.19686 | 89.98% | 0.075 | 2.3 | 1 | 0.58213 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.077175 | 2.345 | 2.6208 | 23.4016 | 28.4445
25 | 283.8 | 61 | 0.20615 | 89.44% | 0.075 | 2.3 | 1 | 0.61674 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.07938 | 2.412 | 2.6957 | 24.793 | 29.98
25 | 283.8 | 62 | 0.21581 | 88.86% | 0.075 | 2.3 | 1 | 0.6536 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.081585 | 2.479 | 2.7706 | 26.2748 | 31.6059
25 | 283.8 | 63 | 0.22586 | 88.26% | 0.075 | 2.3 | 1 | 0.6929 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.08379 | 2.546 | 2.8454 | 27.8546 | 33.3298
25 | 283.8 | 64 | 0.2363 | 87.61% | 0.075 | 2.3 | 1 | 0.73484 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.085995 | 2.613 | 2.9203 | 29.5405 | 35.1598
25 | 283.8 | 65 | 0.24714 | 86.93% | 0.075 | 2.3 | 1 | 0.77964 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.0882 | 2.68 | 2.9952 | 31.3416 | 37.1049
25 | 283.8 | 66 | 0.25841 | 86.2% | 0.075 | 2.3 | 1 | 0.82757 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.090405 | 2.747 | 3.0701 | 33.2681 | 39.1756
25 | 283.8 | 67 | 0.27011 | 85.42% | 0.075 | 2.3 | 1 | 0.8789 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.09261 | 2.814 | 3.145 | 35.3317 | 41.3832
25 | 283.8 | 68 | 0.28225 | 84.59% | 0.075 | 2.3 | 1 | 0.93395 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.094815 | 2.881 | 3.2198 | 37.5449 | 43.7405
25 | 283.8 | 69 | 0.29485 | 83.7% | 0.075 | 2.3 | 1 | 0.99309 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.09702 | 2.948 | 3.2947 | 39.9223 | 46.262
25 | 283.8 | 69.1107 | 0.2963 | 83.6% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.097264 | 2.9554 | 3.303 | 40.2 | 46.5556
25 | 283.8 | 70 | 0.30793 | 83.55% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.099225 | 3.015 | 3.3696 | 40.2 | 46.6838
25 | 283.8 | 71 | 0.32149 | 83.5% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.10143 | 3.082 | 3.4445 | 40.2 | 46.8279
25 | 283.8 | 72 | 0.33556 | 83.45% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.10364 | 3.149 | 3.5194 | 40.2 | 46.9719
25 | 283.8 | 73 | 0.35014 | 83.4% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.10584 | 3.216 | 3.5942 | 40.2 | 47.116
25 | 283.8 | 74 | 0.36525 | 83.35% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.10805 | 3.283 | 3.6691 | 40.2 | 47.2601
25 | 283.8 | 75 | 0.38091 | 83.3% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.11025 | 3.35 | 3.744 | 40.2 | 47.4042
25 | 283.8 | 76 | 0.39713 | 83.25% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.11245 | 3.4169 | 3.8189 | 40.2 | 47.5483
25 | 283.8 | 77 | 0.41392 | 83.2% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.11466 | 3.4839 | 3.8938 | 40.2 | 47.6924
25 | 283.8 | 78 | 0.43132 | 83.14% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.11686 | 3.5509 | 3.9686 | 40.2 | 47.8365
25 | 283.8 | 79 | 0.44932 | 83.09% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.11907 | 3.6179 | 4.0435 | 40.2 | 47.9805
25 | 283.8 | 80 | 0.46794 | 83.04% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.12127 | 3.6849 | 4.1184 | 40.2 | 48.1246
25 | 283.8 | 81 | 0.48722 | 82.99% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.12348 | 3.7519 | 4.1933 | 40.2 | 48.2687
25 | 283.8 | 82 | 0.50715 | 82.94% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.12568 | 3.8189 | 4.2682 | 40.2 | 48.4128
25 | 283.8 | 83 | 0.52777 | 82.89% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.12789 | 3.8859 | 4.343 | 40.2 | 48.5569
25 | 283.8 | 84 | 0.54908 | 82.84% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.13009 | 3.9529 | 4.4179 | 40.2 | 48.701
25 | 283.8 | 85 | 0.5711 | 82.79% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.1323 | 4.0199 | 4.4928 | 40.2 | 48.845
25 | 283.8 | 86 | 0.59386 | 82.74% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.13451 | 4.0869 | 4.5677 | 40.2 | 48.9891
25 | 283.8 | 87 | 0.61738 | 82.69% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.13671 | 4.1539 | 4.6426 | 40.2 | 49.1332
25 | 283.8 | 88 | 0.64167 | 82.64% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.13892 | 4.2209 | 4.7174 | 40.2 | 49.2773
25 | 283.8 | 89 | 0.66675 | 82.59% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.14112 | 4.2879 | 4.7923 | 40.2 | 49.4214
25 | 283.8 | 90 | 0.69264 | 82.54% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.14333 | 4.3549 | 4.8672 | 40.2 | 49.5655
25 | 283.8 | 91 | 0.71937 | 82.48% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.14553 | 4.4219 | 4.9421 | 40.2 | 49.7095
25 | 283.8 | 92 | 0.74695 | 82.43% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.14774 | 4.4889 | 5.017 | 40.2 | 49.8536
25 | 283.8 | 93 | 0.7754 | 82.38% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.14994 | 4.5559 | 5.0918 | 40.2 | 49.9977
25 | 283.8 | 94 | 0.80475 | 82.33% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.15215 | 4.6229 | 5.1667 | 40.2 | 50.1418
25 | 283.8 | 95 | 0.83502 | 82.28% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.15435 | 4.6899 | 5.2416 | 40.2 | 50.2859
25 | 283.8 | 96 | 0.86623 | 82.23% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.15655 | 4.7569 | 5.3165 | 40.2 | 50.43
25 | 283.8 | 97 | 0.8984 | 82.18% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.15876 | 4.8239 | 5.3914 | 40.2 | 50.574
25 | 283.8 | 98 | 0.93156 | 82.13% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.16096 | 4.8909 | 5.4662 | 40.2 | 50.7181
25 | 283.8 | 99 | 0.96572 | 82.08% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.16317 | 4.9579 | 5.5411 | 40.2 | 50.8622
25 | 283.8 | 100 | 1 | 82.03% | 0.075 | 2.3 | 1 | 1 | 0.0294 | 0.02913 | 0.07488 | 40.2 | 0.16537 | 5.0249 | 5.616 | 40.2 | 51.0063

## NSG overview
|  | CH4 reaction |  |  | C2H6 reaction |  |  | C3H8 reaction
|  | CH4 + 2 O2 > CO2 + 2 H2O |  |  | C2H6 + 3.5 O2 > 2 CO2 + 3 H2O |  |  | C3H8 + 5 O2 > 3 CO2 + 4 H2O
|  | CH4 | C2H6 | C3H8 | O2 | N2 | CO2 | H2O
fuel | mol | 0.8 | 0.05 | 0.03 |  | 0.1 | 0.02
air | mol |  |  |  | 2.2138 | 8.855
products | mol |  |  |  | 0.28875 | 8.955 | 1.01 | 1.87
product fraction | % |  |  |  | 2.382% | 73.86% | 8.331% | 15.42%
products | mol |  |  |  | 0.075 | 2.3 | 0 | 1.4221
product fraction | % |  |  |  | 1.975% | 60.57% | 0% | 12.18%
[7 empty] | condensed | 0.23951
HHV | kJ/mol | 890.7 | 1560 | 2250
average HHV | kJ/mol | 858.06
Heat capacity | J/mol/K |  |  |  | 29.4 | 29.13 | 37.1 | 74.88
heat of vaporiation | kJ/mol | [6 empty] | 40.2
inlet temperature | C | 25
outlet temperature | C | 50
non condensed | % | 76.05%
sensible heat | kJ/mol | 0 |  |  | 0.21223 | 6.5215 | 0.93678 | 3.5006 | 11.1711
latent heat | kJ/mol | [6 empty] | 57.1693
total heat | kJ/mol(rxn) | 68.3404
Effective Heating Value | kJ/mol(rxn) | 789.7196 | 92.04%

## NSG eff
Inlet [C] | Combustion [kJ/mol] | Outlet [C] | Partial Pressure | North Sea Gas | O2 mol | N2 mol | CO2 mol | H2O mol | H2O left | O2 Cp | N2 Cp | CO2 Cp | H2O Cp | H2O vap | O2 sensible | N2 sensible | CO2 sensible | H2O sensible | H2O latent | total heat
25 | 858.06 | 0 | 0.006 | 101% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.061894 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.21223 | -6.5215 | -0.93678 | -3.5006 | 2.4881 | -8.683
25 | 888 | 5 | 0.0086 | 100.6% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.088947 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.16978 | -5.2172 | -0.74942 | -2.8005 | 3.5757 | -5.3612
25 | 888 | 10 | 0.0121 | 100.2% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.12559 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.12734 | -3.9129 | -0.56207 | -2.1004 | 5.0487 | -1.654
25 | 888 | 15 | 0.0168 | 99.71% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.17521 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.084892 | -2.6086 | -0.37471 | -1.4003 | 7.0433 | 2.5749
25 | 888 | 20 | 0.0231 | 99.15% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.24246 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.042446 | -1.3043 | -0.18735 | -0.70013 | 9.747 | 7.5128
25 | 888 | 25 | 0.0313 | 98.5% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.33131 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0 | 0 | 0 | 0 | 13.3188 | 13.3188
25 | 888 | 30 | 0.0419 | 97.72% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.44842 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.042446 | 1.3043 | 0.18735 | 0.70013 | 18.0265 | 20.2607
25 | 888 | 35 | 0.0555 | 96.77% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.60252 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.084892 | 2.6086 | 0.37471 | 1.4003 | 24.2214 | 28.6899
25 | 888 | 40 | 0.0728 | 95.6% | 0.28875 | 8.955 | 1.01 | 1.87 | 0.80508 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.12734 | 3.9129 | 0.56207 | 2.1004 | 32.3643 | 39.067
25 | 888 | 45 | 0.0946 | 94.14% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.0714 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.16978 | 5.2172 | 0.74942 | 2.8005 | 43.0685 | 52.0054
25 | 888 | 50 | 0.1218 | 92.3% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.4221 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.21223 | 6.5215 | 0.93678 | 3.5006 | 57.1693 | 68.3404
25 | 888 | 51 | 0.12808 | 91.87% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.5063 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.22072 | 6.7823 | 0.97425 | 3.6407 | 60.5521 | 72.17
25 | 888 | 52 | 0.13453 | 91.43% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.5938 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.22921 | 7.0432 | 1.0117 | 3.7807 | 64.0726 | 76.1374
25 | 888 | 53 | 0.14125 | 90.96% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.6866 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2377 | 7.3041 | 1.0492 | 3.9207 | 67.8007 | 80.3123
25 | 888 | 54 | 0.14826 | 90.46% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.7848 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.24619 | 7.5649 | 1.0867 | 4.0607 | 71.7495 | 84.708
25 | 888 | 55 | 0.15556 | 90.02% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.25468 | 7.8258 | 1.1241 | 4.2008 | 75.174 | 88.5794
25 | 888 | 55.5837 | 0.16 | 90% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.25963 | 7.978 | 1.146 | 4.2825 | 75.174 | 88.8402
25 | 888 | 56 | 0.16317 | 89.97% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.26317 | 8.0866 | 1.1616 | 4.3408 | 75.174 | 89.0262
25 | 888 | 57 | 0.17109 | 89.92% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.27166 | 8.3475 | 1.1991 | 4.4808 | 75.174 | 89.473
25 | 888 | 58 | 0.17934 | 89.87% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.28015 | 8.6084 | 1.2365 | 4.6208 | 75.174 | 89.9199
25 | 888 | 59 | 0.18792 | 89.82% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.28863 | 8.8692 | 1.274 | 4.7609 | 75.174 | 90.3667
25 | 888 | 60 | 0.19686 | 89.77% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.29712 | 9.1301 | 1.3115 | 4.9009 | 75.174 | 90.8136
25 | 888 | 61 | 0.20615 | 89.72% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.30561 | 9.3909 | 1.349 | 5.0409 | 75.174 | 91.2604
25 | 888 | 62 | 0.21581 | 89.67% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.3141 | 9.6518 | 1.3864 | 5.1809 | 75.174 | 91.7073
25 | 888 | 63 | 0.22586 | 89.62% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.32259 | 9.9126 | 1.4239 | 5.321 | 75.174 | 92.1541
25 | 888 | 64 | 0.2363 | 89.57% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.33108 | 10.1735 | 1.4614 | 5.461 | 75.174 | 92.601
25 | 888 | 65 | 0.24714 | 89.52% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.33957 | 10.4344 | 1.4988 | 5.601 | 75.174 | 93.0478
25 | 888 | 66 | 0.25841 | 89.47% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.34806 | 10.6952 | 1.5363 | 5.741 | 75.174 | 93.4946
25 | 888 | 67 | 0.27011 | 89.42% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.35655 | 10.9561 | 1.5738 | 5.8811 | 75.174 | 93.9415
25 | 888 | 68 | 0.28225 | 89.37% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.36504 | 11.2169 | 1.6113 | 6.0211 | 75.174 | 94.3883
25 | 888 | 69 | 0.29485 | 89.32% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.37353 | 11.4778 | 1.6487 | 6.1611 | 75.174 | 94.8352
25 | 888 | 69.1107 | 0.2963 | 89.31% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.37447 | 11.5067 | 1.6529 | 6.1766 | 75.174 | 94.8846
25 | 888 | 70 | 0.30793 | 89.27% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.38202 | 11.7387 | 1.6862 | 6.3012 | 75.174 | 95.282
25 | 888 | 71 | 0.32149 | 89.22% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.39051 | 11.9995 | 1.7237 | 6.4412 | 75.174 | 95.7289
25 | 888 | 72 | 0.33556 | 89.17% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.39899 | 12.2604 | 1.7611 | 6.5812 | 75.174 | 96.1757
25 | 888 | 73 | 0.35014 | 89.12% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.40748 | 12.5212 | 1.7986 | 6.7212 | 75.174 | 96.6226
25 | 888 | 74 | 0.36525 | 89.07% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.41597 | 12.7821 | 1.8361 | 6.8613 | 75.174 | 97.0694
25 | 888 | 75 | 0.38091 | 89.02% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.42446 | 13.043 | 1.8736 | 7.0013 | 75.174 | 97.5162
25 | 888 | 76 | 0.39713 | 88.97% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.43295 | 13.3038 | 1.911 | 7.1413 | 75.174 | 97.9631
25 | 888 | 77 | 0.41392 | 88.92% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44144 | 13.5647 | 1.9485 | 7.2813 | 75.174 | 98.4099
25 | 888 | 78 | 0.43132 | 88.87% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44993 | 13.8255 | 1.986 | 7.4214 | 75.174 | 98.8568
25 | 888 | 79 | 0.44932 | 88.82% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.45842 | 14.0864 | 2.0234 | 7.5614 | 75.174 | 99.3036
25 | 888 | 80 | 0.46794 | 88.77% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.46691 | 14.3473 | 2.0609 | 7.7014 | 75.174 | 99.7505
25 | 888 | 81 | 0.48722 | 88.72% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.4754 | 14.6081 | 2.0984 | 7.8414 | 75.174 | 100.1973
25 | 888 | 82 | 0.50715 | 88.67% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.48389 | 14.869 | 2.1358 | 7.9815 | 75.174 | 100.6442
25 | 888 | 83 | 0.52777 | 88.62% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.49238 | 15.1298 | 2.1733 | 8.1215 | 75.174 | 101.091
25 | 888 | 84 | 0.54908 | 88.57% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.50087 | 15.3907 | 2.2108 | 8.2615 | 75.174 | 101.5379
25 | 888 | 85 | 0.5711 | 88.52% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.50936 | 15.6515 | 2.2483 | 8.4015 | 75.174 | 101.9847
25 | 888 | 86 | 0.59386 | 88.46% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.51784 | 15.9124 | 2.2857 | 8.5416 | 75.174 | 102.4315
25 | 888 | 87 | 0.61738 | 88.41% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.52633 | 16.1733 | 2.3232 | 8.6816 | 75.174 | 102.8784
25 | 888 | 88 | 0.64167 | 88.36% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.53482 | 16.4341 | 2.3607 | 8.8216 | 75.174 | 103.3252
25 | 888 | 89 | 0.66675 | 88.31% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.54331 | 16.695 | 2.3981 | 8.9616 | 75.174 | 103.7721
25 | 888 | 90 | 0.69264 | 88.26% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5518 | 16.9558 | 2.4356 | 9.1017 | 75.174 | 104.2189
25 | 888 | 91 | 0.71937 | 88.21% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.56029 | 17.2167 | 2.4731 | 9.2417 | 75.174 | 104.6658
25 | 888 | 92 | 0.74695 | 88.16% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.56878 | 17.4776 | 2.5106 | 9.3817 | 75.174 | 105.1126
25 | 888 | 93 | 0.7754 | 88.11% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.57727 | 17.7384 | 2.548 | 9.5217 | 75.174 | 105.5595
25 | 888 | 94 | 0.80475 | 88.06% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.58576 | 17.9993 | 2.5855 | 9.6618 | 75.174 | 106.0063
25 | 888 | 95 | 0.83502 | 88.01% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.59425 | 18.2601 | 2.623 | 9.8018 | 75.174 | 106.4531
25 | 888 | 96 | 0.86623 | 87.96% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.60274 | 18.521 | 2.6604 | 9.9418 | 75.174 | 106.9
25 | 888 | 97 | 0.8984 | 87.91% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.61123 | 18.7819 | 2.6979 | 10.0818 | 75.174 | 107.3468
25 | 888 | 98 | 0.93156 | 87.86% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.61972 | 19.0427 | 2.7354 | 10.2219 | 75.174 | 107.7937
25 | 888 | 99 | 0.96572 | 87.81% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.6282 | 19.3036 | 2.7729 | 10.3619 | 75.174 | 108.2405
25 | 888 | 100 | 1 | 87.76% | 0.28875 | 8.955 | 1.01 | 1.87 | 1.87 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.63669 | 19.5644 | 2.8103 | 10.5019 | 75.174 | 108.6874

## H2CH4 overview
| CH4 reaction |  |  |  |  | H2 reaction
| CH4 + 2 O2 > CO2 + 2 H2O |  |  |  |  | H2 + 0.5 O2 > H2O
|  | CH4 | C2H6 | C3H8 | H2 | O2 | N2 | CO2 | H2O
fuel | mol | 0.8 |  |  | 0.2 |  | 0 | 0
air | mol |  |  |  |  | 1.955 | 7.82 | 0.02
products | mol |  |  |  |  | 0.255 | 7.82 | 0.8 | 1.8
product fraction | % |  |  |  |  | 2.389% | 73.26% | 7.494% | 16.86%
products | mol |  |  |  |  | 0.075 | 2.3 | 0 | 1.2309
product fraction | % |  |  |  |  | 2.08% | 63.78% | 0% | 12.18%
[8 empty] | condensed | 0.31617
HHV | kJ/mol | 890.7 | 1560 | 2250 | 285.8
average HHV | kJ/mol | 769.72
Heat capacity | J/mol/K |  |  |  |  | 29.4 | 29.13 | 37.1 | 74.88
heat of vaporiation | kJ/mol | [7 empty] | 40.2
inlet temperature | C | 25
outlet temperature | C | 50
non condensed | % | 68.38%
sensible heat | kJ/mol | 0 |  |  |  | 0.18743 | 5.6949 | 0.742 | 3.3696 | 9.9939
latent heat | kJ/mol | [7 empty] | 49.4821
total heat | kJ/mol(rxn) | 59.4761
Effective Heating Value | kJ/mol(rxn) | 710.2439 | 92.27%

## H2CH4 eff
Inlet [C] | Combustion [kJ/mol] | Outlet [C] | Partial Pressure | 20% H2 in CH4 | O2 mol | N2 mol | CO2 mol | H2O mol | H2O left | O2 Cp | N2 Cp | CO2 Cp | H2O Cp | H2O vap | O2 sensible | N2 sensible | CO2 sensible | H2O sensible | H2O latent | total heat
25 | 769.72 | 0 | 0.006 | 101% | 0.255 | 7.82 | 0.8 | 1.8 | 0.053571 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.18743 | -5.6949 | -0.742 | -3.3696 | 2.1536 | -7.8404
25 | 769.72 | 5 | 0.0086 | 100.6% | 0.255 | 7.82 | 0.8 | 1.8 | 0.076987 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.14994 | -4.5559 | -0.5936 | -2.6957 | 3.0949 | -4.9003
25 | 769.72 | 10 | 0.0121 | 100.2% | 0.255 | 7.82 | 0.8 | 1.8 | 0.1087 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.11245 | -3.4169 | -0.4452 | -2.0218 | 4.3699 | -1.6265
25 | 769.72 | 15 | 0.0168 | 99.73% | 0.255 | 7.82 | 0.8 | 1.8 | 0.15165 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.07497 | -2.278 | -0.2968 | -1.3478 | 6.0962 | 2.0987
25 | 769.72 | 20 | 0.0231 | 99.16% | 0.255 | 7.82 | 0.8 | 1.8 | 0.20986 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.037485 | -1.139 | -0.1484 | -0.67392 | 8.4364 | 6.4376
25 | 769.72 | 25 | 0.0313 | 98.5% | 0.255 | 7.82 | 0.8 | 1.8 | 0.28676 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0 | 0 | 0 | 0 | 11.5279 | 11.5279
25 | 769.72 | 30 | 0.0419 | 97.71% | 0.255 | 7.82 | 0.8 | 1.8 | 0.38812 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.037485 | 1.139 | 0.1484 | 0.67392 | 15.6026 | 17.6014
25 | 769.72 | 35 | 0.0555 | 96.76% | 0.255 | 7.82 | 0.8 | 1.8 | 0.52151 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.07497 | 2.278 | 0.2968 | 1.3478 | 20.9645 | 24.9621
25 | 769.72 | 40 | 0.0728 | 95.58% | 0.255 | 7.82 | 0.8 | 1.8 | 0.69683 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.11245 | 3.4169 | 0.4452 | 2.0218 | 28.0125 | 34.0089
25 | 769.72 | 45 | 0.0946 | 94.12% | 0.255 | 7.82 | 0.8 | 1.8 | 0.9273 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.14994 | 4.5559 | 0.5936 | 2.6957 | 37.2774 | 45.2725
25 | 769.72 | 50 | 0.1218 | 92.27% | 0.255 | 7.82 | 0.8 | 1.8 | 1.2309 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.18743 | 5.6949 | 0.742 | 3.3696 | 49.4821 | 59.4761
25 | 769.72 | 51 | 0.12808 | 91.84% | 0.255 | 7.82 | 0.8 | 1.8 | 1.3037 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.19492 | 5.9227 | 0.77168 | 3.5044 | 52.4101 | 62.8038
25 | 769.72 | 52 | 0.13453 | 91.39% | 0.255 | 7.82 | 0.8 | 1.8 | 1.3795 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.20242 | 6.1505 | 0.80136 | 3.6392 | 55.4572 | 66.2506
25 | 769.72 | 53 | 0.14125 | 90.92% | 0.255 | 7.82 | 0.8 | 1.8 | 1.4598 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.20992 | 6.3783 | 0.83104 | 3.774 | 58.684 | 69.8772
25 | 769.72 | 54 | 0.14826 | 90.43% | 0.255 | 7.82 | 0.8 | 1.8 | 1.5448 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.21741 | 6.6061 | 0.86072 | 3.9087 | 62.1018 | 73.6948
25 | 769.72 | 55 | 0.15556 | 89.9% | 0.255 | 7.82 | 0.8 | 1.8 | 1.6349 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.22491 | 6.8339 | 0.8904 | 4.0435 | 65.7239 | 77.7167
25 | 769.72 | 55.5837 | 0.16 | 89.58% | 0.255 | 7.82 | 0.8 | 1.8 | 1.6905 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.22929 | 6.9669 | 0.90772 | 4.1222 | 67.9571 | 80.1832
25 | 769.72 | 56 | 0.16317 | 89.35% | 0.255 | 7.82 | 0.8 | 1.8 | 1.7305 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.23241 | 7.0617 | 0.92008 | 4.1783 | 69.5645 | 81.957
25 | 769.72 | 57 | 0.17109 | 88.94% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2399 | 7.2895 | 0.94976 | 4.3131 | 72.36 | 85.1522
25 | 769.72 | 58 | 0.17934 | 88.89% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2474 | 7.5173 | 0.97944 | 4.4479 | 72.36 | 85.552
25 | 769.72 | 59 | 0.18792 | 88.83% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2549 | 7.7451 | 1.0091 | 4.5827 | 72.36 | 85.9518
25 | 769.72 | 60 | 0.19686 | 88.78% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.26239 | 7.9729 | 1.0388 | 4.7174 | 72.36 | 86.3515
25 | 769.72 | 61 | 0.20615 | 88.73% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.26989 | 8.2007 | 1.0685 | 4.8522 | 72.36 | 86.7513
25 | 769.72 | 62 | 0.21581 | 88.68% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.27739 | 8.4285 | 1.0982 | 4.987 | 72.36 | 87.151
25 | 769.72 | 63 | 0.22586 | 88.63% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.28489 | 8.6563 | 1.1278 | 5.1218 | 72.36 | 87.5508
25 | 769.72 | 64 | 0.2363 | 88.57% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.29238 | 8.8841 | 1.1575 | 5.2566 | 72.36 | 87.9505
25 | 769.72 | 65 | 0.24714 | 88.52% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.29988 | 9.1119 | 1.1872 | 5.3914 | 72.36 | 88.3503
25 | 769.72 | 66 | 0.25841 | 88.47% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.30738 | 9.3397 | 1.2169 | 5.5261 | 72.36 | 88.7501
25 | 769.72 | 67 | 0.27011 | 88.42% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.31487 | 9.5675 | 1.2466 | 5.6609 | 72.36 | 89.1498
25 | 769.72 | 68 | 0.28225 | 88.37% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.32237 | 9.7953 | 1.2762 | 5.7957 | 72.36 | 89.5496
25 | 769.72 | 69 | 0.29485 | 88.31% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.32987 | 10.0231 | 1.3059 | 5.9305 | 72.36 | 89.9493
25 | 769.72 | 69.1107 | 0.2963 | 88.31% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.3307 | 10.0483 | 1.3092 | 5.9454 | 72.36 | 89.9936
25 | 769.72 | 70 | 0.30793 | 88.26% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.33737 | 10.2508 | 1.3356 | 6.0653 | 72.36 | 90.3491
25 | 769.72 | 71 | 0.32149 | 88.21% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.34486 | 10.4786 | 1.3653 | 6.2001 | 72.36 | 90.7488
25 | 769.72 | 72 | 0.33556 | 88.16% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.35236 | 10.7064 | 1.395 | 6.3348 | 72.36 | 91.1486
25 | 769.72 | 73 | 0.35014 | 88.11% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.35986 | 10.9342 | 1.4246 | 6.4696 | 72.36 | 91.5484
25 | 769.72 | 74 | 0.36525 | 88.05% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.36735 | 11.162 | 1.4543 | 6.6044 | 72.36 | 91.9481
25 | 769.72 | 75 | 0.38091 | 88% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.37485 | 11.3898 | 1.484 | 6.7392 | 72.36 | 92.3479
25 | 769.72 | 76 | 0.39713 | 87.95% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.38235 | 11.6176 | 1.5137 | 6.874 | 72.36 | 92.7476
25 | 769.72 | 77 | 0.41392 | 87.9% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.38984 | 11.8454 | 1.5434 | 7.0088 | 72.36 | 93.1474
25 | 769.72 | 78 | 0.43132 | 87.85% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.39734 | 12.0732 | 1.573 | 7.1436 | 72.36 | 93.5472
25 | 769.72 | 79 | 0.44932 | 87.79% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.40484 | 12.301 | 1.6027 | 7.2783 | 72.36 | 93.9469
25 | 769.72 | 80 | 0.46794 | 87.74% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.41234 | 12.5288 | 1.6324 | 7.4131 | 72.36 | 94.3467
25 | 769.72 | 81 | 0.48722 | 87.69% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.41983 | 12.7566 | 1.6621 | 7.5479 | 72.36 | 94.7464
25 | 769.72 | 82 | 0.50715 | 87.64% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.42733 | 12.9844 | 1.6918 | 7.6827 | 72.36 | 95.1462
25 | 769.72 | 83 | 0.52777 | 87.59% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.43483 | 13.2122 | 1.7214 | 7.8175 | 72.36 | 95.5459
25 | 769.72 | 84 | 0.54908 | 87.53% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44232 | 13.44 | 1.7511 | 7.9523 | 72.36 | 95.9457
25 | 769.72 | 85 | 0.5711 | 87.48% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44982 | 13.6678 | 1.7808 | 8.087 | 72.36 | 96.3455
25 | 769.72 | 86 | 0.59386 | 87.43% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.45732 | 13.8956 | 1.8105 | 8.2218 | 72.36 | 96.7452
25 | 769.72 | 87 | 0.61738 | 87.38% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.46481 | 14.1234 | 1.8402 | 8.3566 | 72.36 | 97.145
25 | 769.72 | 88 | 0.64167 | 87.33% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.47231 | 14.3512 | 1.8698 | 8.4914 | 72.36 | 97.5447
25 | 769.72 | 89 | 0.66675 | 87.28% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.47981 | 14.579 | 1.8995 | 8.6262 | 72.36 | 97.9445
25 | 769.72 | 90 | 0.69264 | 87.22% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.4873 | 14.8068 | 1.9292 | 8.761 | 72.36 | 98.3442
25 | 769.72 | 91 | 0.71937 | 87.17% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.4948 | 15.0346 | 1.9589 | 8.8957 | 72.36 | 98.744
25 | 769.72 | 92 | 0.74695 | 87.12% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5023 | 15.2624 | 1.9886 | 9.0305 | 72.36 | 99.1438
25 | 769.72 | 93 | 0.7754 | 87.07% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5098 | 15.4902 | 2.0182 | 9.1653 | 72.36 | 99.5435
25 | 769.72 | 94 | 0.80475 | 87.02% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.51729 | 15.718 | 2.0479 | 9.3001 | 72.36 | 99.9433
25 | 769.72 | 95 | 0.83502 | 86.96% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.52479 | 15.9458 | 2.0776 | 9.4349 | 72.36 | 100.343
25 | 769.72 | 96 | 0.86623 | 86.91% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.53229 | 16.1736 | 2.1073 | 9.5697 | 72.36 | 100.7428
25 | 769.72 | 97 | 0.8984 | 86.86% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.53978 | 16.4014 | 2.137 | 9.7044 | 72.36 | 101.1425
25 | 769.72 | 98 | 0.93156 | 86.81% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.54728 | 16.6292 | 2.1666 | 9.8392 | 72.36 | 101.5423
25 | 769.72 | 99 | 0.96572 | 86.76% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.55478 | 16.8569 | 2.1963 | 9.974 | 72.36 | 101.9421
25 | 769.72 | 100 | 1 | 86.7% | 0.255 | 7.82 | 0.8 | 1.8 | 1.8 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.56227 | 17.0847 | 2.226 | 10.1088 | 72.36 | 102.3418

## H2NSG overview
| CH4 reaction |  |  | H2 reaction |  | C2H6 reaction |  |  | C3H8 reaction
| CH4 + 2 O2 > CO2 + 2 H2O |  |  | H2 + 0.5 O2 > H2O |  | C2H6 + 3.5 O2 > 2 CO2 + 3 H2O |  |  | C3H8 + 5 O2 > 3 CO2 + 4 H2O
|  | CH4 | C2H6 | C3H8 | H2 | O2 | N2 | CO2 | H2O
fuel | mol | 0.64 | 0.04 | 0.024 | 0.2 |  | 0.08 | 0.016
air | mol |  |  |  |  | 1.886 | 7.544 | 0.02
products | mol |  |  |  |  | 0.246 | 7.624 | 0.808 | 1.696
product fraction | % |  |  |  |  | 2.371% | 73.49% | 7.789% | 16.35%
products | mol |  |  |  |  | 0.075 | 2.3 | 0 | 1.2036
product fraction | % |  |  |  |  | 2.096% | 64.27% | 0% | 12.18%
[8 empty] | condensed | 0.29034
HHV | kJ/mol | 890.7 | 1560 | 2250 | 285.8
average HHV | kJ/mol | 743.608
Heat capacity | J/mol/K |  |  |  |  | 29.4 | 29.13 | 37.1 | 74.88
heat of vaporiation | kJ/mol | [7 empty] | 40.2
inlet temperature | C | 25
outlet temperature | C | 50
non condensed | % | 70.97%
sensible heat | kJ/mol | 0 |  |  |  | 0.18081 | 5.5522 | 0.74942 | 3.1749 | 9.6573
latent heat | kJ/mol | [7 empty] | 48.3838
total heat | kJ/mol(rxn) | 58.0411
Effective Heating Value | kJ/mol(rxn) | 685.5669 | 92.19%

## H2NSG eff
Inlet [C] | Combustion [kJ/mol] | Outlet [C] | Partial Pressure | 20% H2 in NSG | O2 mol | N2 mol | CO2 mol | H2O mol | H2O left | O2 Cp | N2 Cp | CO2 Cp | H2O Cp | H2O vap | O2 sensible | N2 sensible | CO2 sensible | H2O sensible | H2O latent | total heat
25 | 743.608 | 0 | 0.006 | 101% | 0.246 | 7.624 | 0.808 | 1.696 | 0.052382 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.18081 | -5.5522 | -0.74942 | -3.1749 | 2.1058 | -7.5516
25 | 743.608 | 5 | 0.0086 | 100.6% | 0.246 | 7.624 | 0.808 | 1.696 | 0.075278 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.14465 | -4.4417 | -0.59954 | -2.5399 | 3.0262 | -4.6997
25 | 743.608 | 10 | 0.0121 | 100.2% | 0.246 | 7.624 | 0.808 | 1.696 | 0.10629 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.10849 | -3.3313 | -0.44965 | -1.9049 | 4.2729 | -1.5215
25 | 743.608 | 15 | 0.0168 | 99.72% | 0.246 | 7.624 | 0.808 | 1.696 | 0.14828 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.072324 | -2.2209 | -0.29977 | -1.27 | 5.9609 | 2.098
25 | 743.608 | 20 | 0.0231 | 99.15% | 0.246 | 7.624 | 0.808 | 1.696 | 0.2052 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | -0.036162 | -1.1104 | -0.14988 | -0.63498 | 8.2491 | 6.3177
25 | 743.608 | 25 | 0.0313 | 98.48% | 0.246 | 7.624 | 0.808 | 1.696 | 0.2804 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0 | 0 | 0 | 0 | 11.272 | 11.272
25 | 743.608 | 30 | 0.0419 | 97.69% | 0.246 | 7.624 | 0.808 | 1.696 | 0.37951 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.036162 | 1.1104 | 0.14988 | 0.63498 | 15.2563 | 17.1878
25 | 743.608 | 35 | 0.0555 | 96.72% | 0.246 | 7.624 | 0.808 | 1.696 | 0.50993 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.072324 | 2.2209 | 0.29977 | 1.27 | 20.4992 | 24.3621
25 | 743.608 | 40 | 0.0728 | 95.54% | 0.246 | 7.624 | 0.808 | 1.696 | 0.68136 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.10849 | 3.3313 | 0.44965 | 1.9049 | 27.3907 | 33.1851
25 | 743.608 | 45 | 0.0946 | 94.06% | 0.246 | 7.624 | 0.808 | 1.696 | 0.90671 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.14465 | 4.4417 | 0.59954 | 2.5399 | 36.4499 | 44.1758
25 | 743.608 | 50 | 0.1218 | 92.19% | 0.246 | 7.624 | 0.808 | 1.696 | 1.2036 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.18081 | 5.5522 | 0.74942 | 3.1749 | 48.3838 | 58.0411
25 | 743.608 | 51 | 0.12808 | 91.76% | 0.246 | 7.624 | 0.808 | 1.696 | 1.2748 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.18804 | 5.7743 | 0.7794 | 3.3019 | 51.2467 | 61.2903
25 | 743.608 | 52 | 0.13453 | 91.31% | 0.246 | 7.624 | 0.808 | 1.696 | 1.3489 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.19527 | 5.9964 | 0.80937 | 3.4289 | 54.2262 | 64.6561
25 | 743.608 | 53 | 0.14125 | 90.83% | 0.246 | 7.624 | 0.808 | 1.696 | 1.4274 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.20251 | 6.2184 | 0.83935 | 3.5559 | 57.3814 | 68.1976
25 | 743.608 | 54 | 0.14826 | 90.33% | 0.246 | 7.624 | 0.808 | 1.696 | 1.5105 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.20974 | 6.4405 | 0.86933 | 3.6829 | 60.7234 | 71.9258
25 | 743.608 | 55 | 0.15556 | 89.8% | 0.246 | 7.624 | 0.808 | 1.696 | 1.5986 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.21697 | 6.6626 | 0.8993 | 3.8099 | 64.265 | 75.8538
25 | 743.608 | 55.5837 | 0.16 | 89.48% | 0.246 | 7.624 | 0.808 | 1.696 | 1.653 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.22119 | 6.7922 | 0.9168 | 3.884 | 66.4487 | 78.2629
25 | 743.608 | 56 | 0.16317 | 89.24% | 0.246 | 7.624 | 0.808 | 1.696 | 1.692 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2242 | 6.8847 | 0.92928 | 3.9369 | 68.0204 | 79.9955
25 | 743.608 | 57 | 0.17109 | 89.17% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.23144 | 7.1068 | 0.95926 | 4.0639 | 68.1792 | 80.5406
25 | 743.608 | 58 | 0.17934 | 89.12% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.23867 | 7.3289 | 0.98923 | 4.1909 | 68.1792 | 80.9269
25 | 743.608 | 59 | 0.18792 | 89.07% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2459 | 7.551 | 1.0192 | 4.3179 | 68.1792 | 81.3132
25 | 743.608 | 60 | 0.19686 | 89.01% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.25313 | 7.773 | 1.0492 | 4.4449 | 68.1792 | 81.6994
25 | 743.608 | 61 | 0.20615 | 88.96% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.26037 | 7.9951 | 1.0792 | 4.5719 | 68.1792 | 82.0857
25 | 743.608 | 62 | 0.21581 | 88.91% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2676 | 8.2172 | 1.1091 | 4.6989 | 68.1792 | 82.472
25 | 743.608 | 63 | 0.22586 | 88.86% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.27483 | 8.4393 | 1.1391 | 4.8259 | 68.1792 | 82.8583
25 | 743.608 | 64 | 0.2363 | 88.81% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.28206 | 8.6614 | 1.1691 | 4.9529 | 68.1792 | 83.2446
25 | 743.608 | 65 | 0.24714 | 88.75% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.2893 | 8.8835 | 1.1991 | 5.0799 | 68.1792 | 83.6309
25 | 743.608 | 66 | 0.25841 | 88.7% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.29653 | 9.1056 | 1.229 | 5.2069 | 68.1792 | 84.0172
25 | 743.608 | 67 | 0.27011 | 88.65% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.30376 | 9.3277 | 1.259 | 5.3339 | 68.1792 | 84.4035
25 | 743.608 | 68 | 0.28225 | 88.6% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.31099 | 9.5497 | 1.289 | 5.4608 | 68.1792 | 84.7898
25 | 743.608 | 69 | 0.29485 | 88.55% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.31823 | 9.7718 | 1.319 | 5.5878 | 68.1792 | 85.1761
25 | 743.608 | 69.1107 | 0.2963 | 88.54% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.31903 | 9.7964 | 1.3223 | 5.6019 | 68.1792 | 85.2188
25 | 743.608 | 70 | 0.30793 | 88.49% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.32546 | 9.9939 | 1.349 | 5.7148 | 68.1792 | 85.5624
25 | 743.608 | 71 | 0.32149 | 88.44% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.33269 | 10.216 | 1.3789 | 5.8418 | 68.1792 | 85.9487
25 | 743.608 | 72 | 0.33556 | 88.39% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.33992 | 10.4381 | 1.4089 | 5.9688 | 68.1792 | 86.335
25 | 743.608 | 73 | 0.35014 | 88.34% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.34716 | 10.6602 | 1.4389 | 6.0958 | 68.1792 | 86.7213
25 | 743.608 | 74 | 0.36525 | 88.29% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.35439 | 10.8823 | 1.4689 | 6.2228 | 68.1792 | 87.1075
25 | 743.608 | 75 | 0.38091 | 88.23% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.36162 | 11.1044 | 1.4988 | 6.3498 | 68.1792 | 87.4938
25 | 743.608 | 76 | 0.39713 | 88.18% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.36885 | 11.3264 | 1.5288 | 6.4768 | 68.1792 | 87.8801
25 | 743.608 | 77 | 0.41392 | 88.13% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.37608 | 11.5485 | 1.5588 | 6.6038 | 68.1792 | 88.2664
25 | 743.608 | 78 | 0.43132 | 88.08% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.38332 | 11.7706 | 1.5888 | 6.7308 | 68.1792 | 88.6527
25 | 743.608 | 79 | 0.44932 | 88.03% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.39055 | 11.9927 | 1.6187 | 6.8578 | 68.1792 | 89.039
25 | 743.608 | 80 | 0.46794 | 87.97% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.39778 | 12.2148 | 1.6487 | 6.9848 | 68.1792 | 89.4253
25 | 743.608 | 81 | 0.48722 | 87.92% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.40501 | 12.4369 | 1.6787 | 7.1118 | 68.1792 | 89.8116
25 | 743.608 | 82 | 0.50715 | 87.87% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.41225 | 12.659 | 1.7087 | 7.2388 | 68.1792 | 90.1979
25 | 743.608 | 83 | 0.52777 | 87.82% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.41948 | 12.8811 | 1.7387 | 7.3658 | 68.1792 | 90.5842
25 | 743.608 | 84 | 0.54908 | 87.77% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.42671 | 13.1031 | 1.7686 | 7.4928 | 68.1792 | 90.9705
25 | 743.608 | 85 | 0.5711 | 87.71% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.43394 | 13.3252 | 1.7986 | 7.6198 | 68.1792 | 91.3568
25 | 743.608 | 86 | 0.59386 | 87.66% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44118 | 13.5473 | 1.8286 | 7.7468 | 68.1792 | 91.7431
25 | 743.608 | 87 | 0.61738 | 87.61% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.44841 | 13.7694 | 1.8586 | 7.8738 | 68.1792 | 92.1294
25 | 743.608 | 88 | 0.64167 | 87.56% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.45564 | 13.9915 | 1.8885 | 8.0008 | 68.1792 | 92.5156
25 | 743.608 | 89 | 0.66675 | 87.51% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.46287 | 14.2136 | 1.9185 | 8.1278 | 68.1792 | 92.9019
25 | 743.608 | 90 | 0.69264 | 87.45% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.47011 | 14.4357 | 1.9485 | 8.2548 | 68.1792 | 93.2882
25 | 743.608 | 91 | 0.71937 | 87.4% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.47734 | 14.6577 | 1.9785 | 8.3818 | 68.1792 | 93.6745
25 | 743.608 | 92 | 0.74695 | 87.35% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.48457 | 14.8798 | 2.0084 | 8.5088 | 68.1792 | 94.0608
25 | 743.608 | 93 | 0.7754 | 87.3% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.4918 | 15.1019 | 2.0384 | 8.6358 | 68.1792 | 94.4471
25 | 743.608 | 94 | 0.80475 | 87.25% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.49904 | 15.324 | 2.0684 | 8.7628 | 68.1792 | 94.8334
25 | 743.608 | 95 | 0.83502 | 87.19% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.50627 | 15.5461 | 2.0984 | 8.8898 | 68.1792 | 95.2197
25 | 743.608 | 96 | 0.86623 | 87.14% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5135 | 15.7682 | 2.1284 | 9.0168 | 68.1792 | 95.606
25 | 743.608 | 97 | 0.8984 | 87.09% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.52073 | 15.9903 | 2.1583 | 9.1437 | 68.1792 | 95.9923
25 | 743.608 | 98 | 0.93156 | 87.04% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.52797 | 16.2124 | 2.1883 | 9.2707 | 68.1792 | 96.3786
25 | 743.608 | 99 | 0.96572 | 86.99% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.5352 | 16.4344 | 2.2183 | 9.3977 | 68.1792 | 96.7649
25 | 743.608 | 100 | 1 | 86.94% | 0.246 | 7.624 | 0.808 | 1.696 | 1.696 | 0.0294 | 0.02913 | 0.0371 | 0.07488 | 40.2 | 0.54243 | 16.6565 | 2.2483 | 9.5247 | 68.1792 | 97.1512