## overview
Start with gas phase fuel (CH4 or H2) and 15% excess air (N2 and O2) at 25’C and 1bar
End with the CO2, H2O, O2, and N2 products at a constant flue gas temperature and 1 bar
But what flue gas temperature do we use?
Bases on https://www.heatgeek.com/condensing-boilers-efficiency/
(Which is itself referencing https://www.ashrae.org/about/news/2016/ashrae-2016-handbook-focuses-on-hvac-systems-and-equipment)
56.02'C is the flue gas dew point temperature (H2O vapour pressure of 0.1667 bar))
To get condensation, need flue gas temperature below this
Amount of condensation is non-linear, as dew point changes as dew condenses out
at 50'C the vapour pressure of H2O is 0.1265 bar
corresponds to about 27% of the H2O having condensed out of the gas phase
THEREFORE the outlet conditions of a condensing boiler is 50'C flue gas and 27% condensation
Higher Heating Value (HHV) has a specific meaning:
bringing all the products down to pre-combustion temperature, and condensing all vapour
Lower Heating Value (LHV) has no aggreed on meaning, but most commonly it is HHV - vaporisation of H2O
CH4 properties
https://webbook.nist.gov/cgi/cbook.cgi?ID=C74828&Mask=1
the rest I just took from Wolfram Alpha

## thermodynamic data
master table of thermodynamic data values, with references and at specified temperatures are pressures
heat capacity at 8C and 1.05325 (40 mbarg) from NIST
https://webbook.nist.gov/chemistry/name-ser/
HHV at 25C and 1 atm from
https://nvlpubs.nist.gov/nistpubs/TechnicalNotes/NIST.TN.2126.pdf
Tc, Pc, omega, Mw from somewhere, put into the P-R EoS
viscosity from somewhere
[10 empty] | (as n-hexane) |  | (pseudo-comp) |  |  | gas as a whole
Fundamental property | units | C1 | C2 | C3 | nC4 | iC4 | nC5 | iC5 | neoC5 | C6+ |  | combustibles | CO2 | N2 | NTS | H2 | O2 | H2O (gas) | H2O (liq)
HHV | kJ/mol | 890.602 | 1560.39 | 2218.66 | 2868.41 | 2877.28 | 3536.09 | 3529.17 | 3514.95 | 4194.75 |  | 970.0075 |  |  | 940.8132 | 285.826 |  |  | 43.99 | < this value is actually heat of vaporisation at 25C, by https://www.engineeringtoolbox.com/water-properties-d_1573.html
Heat capacity | J/mol/K | 35.3124 | 50.725 | 70.1256 | 94.0345 | 91.8862 | 114.7864 | 113.0996 | 114.574 | 136.446 |  | 37.376 | 36.2775 | 29.1181 | 37.276 | 28.7557 | 29.3372 | 32.8126 | 75.6328 | interpolated from NIST data tables
Tc | K | 190.56 | 305.32 | 369.15 | 425 | 407.7 | 469.8 | 461 | 433.8 | 507.6 |  |  | 304.2 | 126.21 | 7.4906 | 33.2 | 154.581 | 647.1
Pc | Pa | 45.99 | 48.72 | 42.48 | 38 | 36.5 | 33.6 | 33.8 | 31.963 | 30.2 |  |  | 73.8 | 33.958 | 1.8485 | 13 | 50.43 | 220.6
omega (PR) | - | 0.01142 | 0.099 | 0.1521 | 0.20081 | 0.18353 | 0.25103 | 0.2274 | 0.1961 | 0.1521 |  |  | 0.228 | 0.0372 | 0.0050774 | -0.22 | 0.022 | 0.34429
viscosity | Pa s | 1.0649e-05 | 9.0761e-06 | 7.8984e-06 | 7.2183e-06 | 7.2206e-06 | 6.4353e-06 | 6.4509e-06 | 6.6757e-06 | 6.1346e-06 |  | 1.0488e-05 | 1.4482e-05 | 1.7432e-05 | 1.0636e-05 | 8.6552e-06 | 2.0108e-05 | 9.3822e-06 |  | interpolated at 15C from the data in the PR code
Mw | g/mol | 16.0425 | 30.07 | 44.096 | 58.1222 | 58.1222 | 72.1488 | 72.1488 | 72.1488 | 86.1754 |  | 17.7174 | 44.01 | 28.013 | 18.3591 | 2.015 | 31.9988 | 18.015
Derived properties
NTS gas mole fraction | - | 89.55% | 5.12% | 1.355% | 0.1269% | 0.2162% | 0.002% | 0.0344% | 0.3472% | 0.2377% |  | 96.99% | 2.074% | 0.9354% |  |  | Synthetic Air
Carbon atoms | - | 1 | 2 | 3 | 4 | 4 | 5 | 5 | 5 | 6 |  | 1.1194 | 0 | 0 |  |  | 20.95% | O2 | https://chem.libretexts.org/Bookshelves/Environmental_Chemistry/Geochemistry_(Lower)/03%3A_The_Atmosphere/3.01%3A_Structure_and_Composition_of_the_Atmosphere
Hydrogen atoms | - | 4 | 6 | 8 | 10 | 10 | 12 | 12 | 12 | 14 |  | 4.2388 | 0 | 0 |  |  | 79.05% | N2
C_ |  | 0.89551 | 0.10239 | 0.040647 | 0.005076 | 0.008648 | 0.0001 | 0.00172 | 0.01736 | 0.014262 | 1.0857 | 1.1194 |  |  |  |  | 0% | H20 | I know these dont add up to 1, but it makes no difference anyway
H_ |  | 3.5821 | 0.30718 | 0.10839 | 0.01269 | 0.02162 | 0.00024 | 0.004128 | 0.041664 | 0.033278 | 4.1112 | 4.2388
[10 empty] | O2: fuel ratio |  | 2.1791 |  | O2: gas ratio | 2.1135 |  |  |  | it would make marginally less than no difference if done "properly"
Properties of combustion | [14 empty] | CO2 per fuel | 1.1065
2.0556

## vapour pressure data
Temp [C] | Vapour pressure [atm] |  | Antoine %atn | Diff | Antoine (mm/Hg) |  | Sonntag | Sonntag Diff | T (K) | 1/T | T^2 | ln(T) | Antoine coeff.
0 | 0.006 | https://en.wikipedia.org/wiki/Vapour_pressure_of_water | 0.0013158 | -0.0046842 | 1 | 0.65727 | 0.0060322 | 3.2202e-05 | 273.15 | 0.003661 | 74610.9225 | 5.61 | A | 8.0713
5 | 0.0086 |  | 0.0059766 | -0.0026234 | 4.5422 | 0.81275 | 0.0086113 | 1.1296e-05 | 278.15 | 0.0035952 | 77367.4225 | 5.6282 | B | 1730.63
10 | 0.0121 |  | 0.0085494 | -0.0035506 | 6.4975 | 0.96184 | 0.012121 | 2.0734e-05 | 283.15 | 0.0035317 | 80173.9225 | 5.646 | C | 233.426
15 | 0.0168 |  | 0.012051 | -0.0047489 | 9.1588 | 1.1049 | 0.016834 | 3.4082e-05 | 288.15 | 0.0034704 | 83030.4225 | 5.6635 |  | valid < 99C
20 | 0.0231 |  | 0.016754 | -0.0063461 | 12.733 | 1.2424 | 0.023087 | -1.3406e-05 | 293.15 | 0.0034112 | 85936.9225 | 5.6807 | 1 atm | 759.9999 | mmHg
25 | 0.0313 |  | 0.022991 | -0.0083089 | 17.4733 | 1.3745 | 0.031285 | -1.548e-05 | 298.15 | 0.003354 | 88893.4225 | 5.6976
30 | 0.0419 |  | 0.031166 | -0.010734 | 23.6864 | 1.5016 | 0.041915 | 1.4919e-05 | 303.15 | 0.0032987 | 91899.9225 | 5.7142 | Sonntag Perry p1325)
35 | 0.0555 |  | 0.041763 | -0.013737 | 31.7402 | 1.624 | 0.055556 | 5.5907e-05 | 308.15 | 0.0032452 | 94956.4225 | 5.7306 |  | -6096.9385
40 | 0.0728 |  | 0.055357 | -0.017443 | 42.0711 | 1.7419 | 0.072887 | 8.7203e-05 | 313.15 | 0.0031934 | 98062.9225 | 5.7467 |  | 21.241
45 | 0.0946 |  | 0.072622 | -0.021978 | 55.1928 | 1.8555 | 0.094701 | 0.00010086 | 318.15 | 0.0031432 | 101219.4225 | 5.7625 |  | -0.027112
50 | 0.1218 |  | 0.094348 | -0.027452 | 71.7046 | 1.9652 | 0.12191 | 0.0001121 | 323.15 | 0.0030945 | 104425.9225 | 5.7781 |  | 1.674e-05
51 | 0.12808 | https://www.spiraxsarco.com/resources-and-design-tools/steam-tables/saturated-water-line#article-top | 0.12145 | -0.0066368 | 92.2999 | 1.9867 | 0.12809 | 7.8965e-06 | 324.15 | 0.003085 | 105073.2225 | 5.7812 |  | 2.4335
52 | 0.13453 |  | 0.1276 | -0.0069275 | 96.9771 | 2.008 | 0.13454 | 9.1663e-06 | 325.15 | 0.0030755 | 105722.5225 | 5.7843
53 | 0.14125 |  | 0.13402 | -0.0072298 | 101.8561 | 2.0292 | 0.14126 | 9.2074e-06 | 326.15 | 0.0030661 | 106373.8225 | 5.7874
54 | 0.14826 |  | 0.14072 | -0.0075423 | 106.9439 | 2.0502 | 0.14827 | 9.5585e-06 | 327.15 | 0.0030567 | 107027.1225 | 5.7904
55 | 0.15556 |  | 0.14769 | -0.0078656 | 112.2477 | 2.0711 | 0.15557 | 9.9993e-06 | 328.15 | 0.0030474 | 107682.4225 | 5.7935
56 | 0.16317 |  | 0.15497 | -0.0081998 | 117.7751 | 2.0918 | 0.16318 | 1.0554e-05 | 329.15 | 0.0030381 | 108339.7225 | 5.7965
56.3747 | 0.16614 | interpolated, dew point temperature of NTSg combustion | 0.16254 | -0.0035915 | 123.5336 | 2.0995 | 0.16611 | -2.6602e-05 | 329.5247 | 0.0030347 | 108586.553 | 5.7977
57 | 0.17109 |  | 0.16546 | -0.005625 | 125.7526 | 2.1124 | 0.1711 | 1.1495e-05 | 330.15 | 0.0030289 | 108999.0225 | 5.7995
58 | 0.17934 |  | 0.17044 | -0.0089024 | 129.531 | 2.1328 | 0.17935 | 1.1344e-05 | 331.15 | 0.0030198 | 109660.3225 | 5.8026
59 | 0.18792 |  | 0.17865 | -0.009271 | 135.7755 | 2.1531 | 0.18793 | 1.188e-05 | 332.15 | 0.0030107 | 110323.6225 | 5.8056
60 | 0.19686 |  | 0.1872 | -0.0096519 | 142.2751 | 2.1733 | 0.19687 | 1.2136e-05 | 333.15 | 0.0030017 | 110988.9225 | 5.8086
61 | 0.20615 |  | 0.1961 | -0.010045 | 149.0384 | 2.1933 | 0.20616 | 1.2406e-05 | 334.15 | 0.0029927 | 111656.2225 | 5.8116
62 | 0.21581 |  | 0.20536 | -0.010449 | 156.074 | 2.2132 | 0.21582 | 1.325e-05 | 335.15 | 0.0029837 | 112325.5225 | 5.8146
63 | 0.22586 |  | 0.21499 | -0.010867 | 163.3906 | 2.233 | 0.22587 | 1.3492e-05 | 336.15 | 0.0029749 | 112996.8225 | 5.8176
64 | 0.2363 |  | 0.225 | -0.011298 | 170.9974 | 2.2526 | 0.23631 | 1.3227e-05 | 337.15 | 0.002966 | 113670.1225 | 5.8205
65 | 0.24714 |  | 0.2354 | -0.011742 | 178.9036 | 2.2721 | 0.24715 | 1.3822e-05 | 338.15 | 0.0029573 | 114345.4225 | 5.8235
66 | 0.25841 |  | 0.24621 | -0.012198 | 187.1186 | 2.2915 | 0.25842 | 1.3921e-05 | 339.15 | 0.0029485 | 115022.7225 | 5.8264
67 | 0.27011 |  | 0.25744 | -0.012669 | 195.6521 | 2.3107 | 0.27012 | 1.3444e-05 | 340.15 | 0.0029399 | 115702.0225 | 5.8294
68 | 0.28225 |  | 0.2691 | -0.013152 | 204.5142 | 2.3298 | 0.28226 | 1.3596e-05 | 341.15 | 0.0029313 | 116383.3225 | 5.8323
69 | 0.29485 |  | 0.2812 | -0.013649 | 213.7147 | 2.3488 | 0.29487 | 1.3864e-05 | 342.15 | 0.0029227 | 117066.6225 | 5.8352
70 | 0.30793 |  | 0.29377 | -0.01416 | 223.2643 | 2.3677 | 0.30794 | 1.4023e-05 | 343.15 | 0.0029142 | 117751.9225 | 5.8382
70.0201 | 0.3082 | interpolated, dew point temperature of H2 combustion | 0.30681 | -0.0013945 | 233.1733 | 2.3681 | 0.30821 | 9.1835e-06 | 343.1701 | 0.002914 | 117765.7139 | 5.8382
71 | 0.32149 |  | 0.30707 | -0.014418 | 233.3762 | 2.3864 | 0.32151 | 1.4138e-05 | 344.15 | 0.0029057 | 118439.2225 | 5.8411
72 | 0.33556 |  | 0.32033 | -0.015225 | 243.4526 | 2.405 | 0.33557 | 1.3567e-05 | 345.15 | 0.0028973 | 119128.5225 | 5.844
73 | 0.35014 |  | 0.33436 | -0.015778 | 254.1134 | 2.4235 | 0.35015 | 1.2964e-05 | 346.15 | 0.0028889 | 119819.8225 | 5.8469
74 | 0.36525 |  | 0.3489 | -0.016345 | 265.1667 | 2.4419 | 0.36526 | 1.328e-05 | 347.15 | 0.0028806 | 120513.1225 | 5.8498
75 | 0.38091 |  | 0.36398 | -0.016928 | 276.6242 | 2.4601 | 0.38092 | 1.2769e-05 | 348.15 | 0.0028723 | 121208.4225 | 5.8526
76 | 0.39713 |  | 0.3796 | -0.017525 | 288.4977 | 2.4783 | 0.39714 | 1.1986e-05 | 349.15 | 0.0028641 | 121905.7225 | 5.8555
77 | 0.41392 |  | 0.39579 | -0.018136 | 300.799 | 2.4963 | 0.41394 | 1.1793e-05 | 350.15 | 0.0028559 | 122605.0225 | 5.8584
78 | 0.43132 |  | 0.41255 | -0.018762 | 313.5406 | 2.5142 | 0.43133 | 1.1362e-05 | 351.15 | 0.0028478 | 123306.3225 | 5.8612
79 | 0.44932 |  | 0.42991 | -0.019402 | 326.7347 | 2.532 | 0.44933 | 1.1175e-05 | 352.15 | 0.0028397 | 124009.6225 | 5.8641
80 | 0.46794 |  | 0.44789 | -0.020057 | 340.3943 | 2.5497 | 0.46796 | 1.1027e-05 | 353.15 | 0.0028317 | 124714.9225 | 5.8669
81 | 0.48722 |  | 0.46649 | -0.020727 | 354.5323 | 2.5672 | 0.48723 | 1.0031e-05 | 354.15 | 0.0028237 | 125422.2225 | 5.8697
82 | 0.50715 |  | 0.48574 | -0.021412 | 369.1619 | 2.5847 | 0.50716 | 9.6143e-06 | 355.15 | 0.0028157 | 126131.5225 | 5.8725
83 | 0.52777 |  | 0.50565 | -0.022112 | 384.2966 | 2.602 | 0.52777 | 8.5291e-06 | 356.15 | 0.0028078 | 126842.8225 | 5.8754
84 | 0.54908 |  | 0.52625 | -0.022826 | 399.9502 | 2.6192 | 0.54908 | 7.8483e-06 | 357.15 | 0.0027999 | 127556.1225 | 5.8782
85 | 0.5711 |  | 0.54755 | -0.023554 | 416.1368 | 2.6364 | 0.57111 | 6.9702e-06 | 358.15 | 0.0027921 | 128271.4225 | 5.881
86 | 0.59386 |  | 0.56957 | -0.024297 | 432.8706 | 2.6534 | 0.59387 | 6.6205e-06 | 359.15 | 0.0027844 | 128988.7225 | 5.8837
87 | 0.61738 |  | 0.59232 | -0.025055 | 450.1661 | 2.6703 | 0.61738 | 5.8544e-06 | 360.15 | 0.0027766 | 129708.0225 | 5.8865
88 | 0.64167 |  | 0.61584 | -0.025827 | 468.0383 | 2.6871 | 0.64167 | 5.0585e-06 | 361.15 | 0.0027689 | 130429.3225 | 5.8893
89 | 0.66675 |  | 0.64013 | -0.026613 | 486.5021 | 2.7038 | 0.66675 | 4.953e-06 | 362.15 | 0.0027613 | 131152.6225 | 5.8921
90 | 0.69264 |  | 0.66523 | -0.027412 | 505.5729 | 2.7204 | 0.69264 | 4.5938e-06 | 363.15 | 0.0027537 | 131877.9225 | 5.8948
91 | 0.71937 |  | 0.69114 | -0.028226 | 525.2664 | 2.7369 | 0.71937 | 4.3743e-06 | 364.15 | 0.0027461 | 132605.2225 | 5.8976
92 | 0.74695 |  | 0.71789 | -0.029053 | 545.5985 | 2.7533 | 0.74695 | 4.0274e-06 | 365.15 | 0.0027386 | 133334.5225 | 5.9003
93 | 0.7754 |  | 0.74551 | -0.029894 | 566.5854 | 2.7696 | 0.7754 | 3.6276e-06 | 366.15 | 0.0027311 | 134065.8225 | 5.903
94 | 0.80475 |  | 0.774 | -0.030747 | 588.2434 | 2.7857 | 0.80476 | 3.5923e-06 | 367.15 | 0.0027237 | 134799.1225 | 5.9058
95 | 0.83502 |  | 0.80341 | -0.031614 | 610.5894 | 2.8018 | 0.83502 | 3.6842e-06 | 368.15 | 0.0027163 | 135534.4225 | 5.9085
96 | 0.86623 |  | 0.83374 | -0.032491 | 633.6405 | 2.8178 | 0.86623 | 5.0129e-06 | 369.15 | 0.0027089 | 136271.7225 | 5.9112
97 | 0.8984 |  | 0.86502 | -0.033383 | 657.4138 | 2.8337 | 0.89841 | 5.0364e-06 | 370.15 | 0.0027016 | 137011.0225 | 5.9139
98 | 0.93156 |  | 0.89727 | -0.034284 | 681.927 | 2.8495 | 0.93156 | 6.563e-06 | 371.15 | 0.0026943 | 137752.3225 | 5.9166
99 | 0.96572 |  | 0.93052 | -0.035197 | 707.198 | 2.8652 | 0.96573 | 8.7529e-06 | 372.15 | 0.0026871 | 138495.6225 | 5.9193
100 | 1 |  | 0.9648 | -0.035204 | 733.245 | 2.8809 | 1.0009 | 0.00092812 | 373.15 | 0.0026799 | 139240.9225 | 5.922

## formatted tables
These are the tables which appear in the paper. We do not use a hand calculator.
All combustion energies are Higher Heating Values at 298K and 1 atm.
ΔH (kJ/mol)
H2 | 285.826
NG | 940.8132
H2/NG | 0.30381
reciprocal | 3.2916
Rgas | 8.3145 | J/mol/K
|  |  |  | 8C | 8C | 15C | 15C | 8C
| ΔH (kJ/mol) | Mw (g/mol) | ΔH (kJ/g) | Rho (kg/m3) | ΔH (kJ/m3) | Rho (kg/m3) | ΔH (kJ/m3) | Z
H2 | 285.826 | 2.015 | 141.8491 | 0.09141 | 12966.4291 | 0.08919 | 12651.524 | 1.0003
CH4 | 890.602 | 16.0425 | 55.5153 | 0.73004 | 40528.3905 | 0.71217 | 39536.3321 | 0.99716
NG | 940.8132 | 18.3591 | 51.245 | 0.83556 | 42818.276 | 0.85852 | 43994.8613 | 0.99705
H2/CH4 | 3.1159 | 7.9615 | 2.5551 | 7.9864 | 3.1256 | 7.9849 | 3.125 | 1.0031
H2/NG | 0.30381 | 9.1112 | 2.7681 | 9.1408 | 3.3022 | 9.6257 | 3.4774 | 1.0032
|  |  |  | ^ calculation from PR |  | ^ calculation from PR |  | ^ calculation from PR?
[5 empty] | ^ derived property from rho |  | ^ derived property from rho
these derived deltaH in kJ/m3 are only useful as a comparison to someone who is already familiar with HHV
and is used to seeing it in these units
it is not useful to our calculations at all, and may confuse matters more
the ratio of it is exactly the ratio in molar form, times the Z ratio
average efficiency of existing boilers |  |  |  |  | 0.30479
% of boilers | efficiency
4% | 91.22% | well adjusted condensing boilers, 50C flue
86% | 87.46% | badly adjusted condensing boilers, 70C flue
10% | 86.23% | non condensing boilers, 100C flue
OVERALL | 87.49% | average efficiency of existing NG boilers
| 93.39% | efficiency of H2 boiler, 50C flue
efficiency ratio | 1.0675 | eta_50C_H2 / eta__average_NG
efficiency ratio | 1.0238 | eta_50C_H2 / eta_50C_NG
Velocity ratio |  | Z ratio |  |  |  | 1.0032 |  |  | 3.0935
| HHV ratio | Pav ratio | eff ratio |  | 0.30381 | 1 | 1.0675
[6 empty] | 1.0032 |  |  | 3.0764
P ressure drop =∝ ρ3/4.v7/4.μ1/4 |  |  |  |  | 0.30381 | 1.0056 | 1.0675
NG rho | 0.83556 |  | 8 C
H2 rho | 0.09141 |  | 8 C
rho ratio | 0.1094
rho^3/4 ratio | 0.19022
NG mu | 10.3739 | microPa.s | 8 C
H2 mu | 8.5092 | microPa.s | 8 C
mu ratio | 0.82025
mu^1/4 ratio | 0.95167
rho^3/4 .mu^1/4 ratio | 0.18103
HHV condensing boiler correction
|  | ΔH (kJ/mol) ratio | Z ratio | mean P ratio | Boiler effc. ratio |  |  |  | in the fully laminar regume
velocity ratio | 3.0764 | 0.30381 | 1.0032 | 1.0056 | 1.0675
vr^7/4 | 7.146 |  |  | ^ above value is a guess |  |  |  |  | delta P ratio | 2.5234
vr^11/4 | 21.9836 | [7 empty] | W ratio | 7.7628
1 atm | 1.0132 | bar
Pressure drop ratio = | 1.2936 | x | [6 empty] | In the fully turbulent regime
high | 60 | mbarg
low | 20 | mbarg | < low end pressure stays at 20mbarg | [5 empty] | delta P ratio | 1.0354
drop | 40 | mbarg | [6 empty] | W ratio | 3.1851
mean P | 1.0533 | bar
new drop | 51.7453 | mbarg
new mean P | 45.8727 | mbarg | [6 empty] | Reynolds ratio
new mean P | 1.0591 | bar |  | iteration |  |  |  |  | 0.41031
mean P ratio | 1.0056 | < this value is calculated |  | 1.0056
Power ratio | 3.9797 |  |  | ^ this value is what the guess should be changed to
3.9797
30 kW natural gas as a velocity (previously 6m3/hr as velocity) |  |  |  |  | As H2
diamter | 35 | mm
area | 0.00096211 | m^2
energy flow Q | 30 | kW
Z | 0.99705
Rgas | 8.3145 | J/mol/K
T | 281.15 | K
P | 105325 | Pa
HHV | 940813.1853 | J/mol
eta | 87.49% |  |  |  | use velocity ratio
velocity | 0.8383 | m/s | (Q Z R T) / (A P HHV eta) |  | 2.5789 | m/s
rho | 0.83556 | kg/m3 |  |  | 0.09141 | kg/m3
mu | 10.3739 | microPa.s | 8 C |  | 8.5092 | microPa.s
Re | 2363.2132 | pipe | rho.v.D/mu |  | 969.6393 | pipe
volume flow | 0.00080654 | m3/s |  |  | 0.0024812 | m3/s
| 2.9035 | m3/hr | half the flow |  | 8.9323 | m3/hr
Calc. length of in-road pipe as 16km
diameter | 110 | mm | Now a bigger pipe, for multiple houses
single house | 0.0010269 | m3/s | 3.6969 | m3/hour
# of houses | 30
total flow | 0.030808 | m3/s | 110.9071 | m3/hour
pipe area | 0.0095033 | m2
velocity | 3.2418 | m/s
p1 | 75 | mbar
p2 | 20 | mbar
p_drop | 0.055 | bar
mean p | 1.0608 | bar
NG rho | 0.84148 | kg/m3 | at [ mean p ]
NG mu | 10.3739 | microPa.s | at [ mean p ]
Re | 28925.1618 | pipe | rho.v.D/mu
|  | 2.dP/0.079 | rho^-3/4 | v^-7/4 | D^5/4 | mu^-1/4
L (m) | 5397.766 | 139240.5063 | 1.1382 | 0.12768 | 0.015139 | 17.6203
If that was in 2004, then in 2021 we have less
2004 | 34035 | toe
2021 | 26275 | toe
vol. ratio | 1.2953 | 0.772
velocity | 0.64717 | m/s | in 2021
vol ratio^-7/4 | 0.63581
p drop | 34.9697 | mbar | in 2021
exit p | 40.0303 | mbar | in 2021
headroom | 20.0303 | mbar | in 2021
Re | 5733.8261 | using the same mean p for rho and mu as for 2004 which is not quite right
H2 p drop | 45.238 | mbar
H2 exit p | 29.762 | mbar
H2 headroom | 9.762 | mbar | A bit too close for comfort.
H2 velocity | 1.9909 | m/s | rho | v | D | mu (Pa.s)
H2 Re | 2352.6202 |  | 0.09141 | 1.9909 | 0.11 | 8.5092e-06
6 cubic metres of gas at 8 C is how much power?
6 | m3/hour
42818.276 | kJ/m3 | at 8C
256909.6557 | kJ/hour
71.3638 | kJ/s | ie kW

## test figure Pressure ratio
f | Re |  | Re (NG) | Re (H2) | f (NG) | f (H2) - approx | f ratio | Delta P ratio | W ratio
0.255 | 251.1886 |  | 251.1886 | 103.0641 | 0.255 | 0.62097 | 2.4352 | 2.5213 | 7.7563
0.236 | 271.1227 |  | 271.1227 | 111.2431 | 0.236 | 0.57532 | 2.4378 | 2.524 | 7.7646
0.219 | 292.6386 |  | 292.6386 | 120.0712 | 0.219 | 0.53302 | 2.4339 | 2.5199 | 7.7521
0.203 | 315.8621 | rho ratio | 315.8621 | 129.5999 | 0.203 | 0.49383 | 2.4326 | 2.5186 | 7.7482
0.188 | 340.9285 | 0.1094 | 340.9285 | 139.8848 | 0.188 | 0.45752 | 2.4336 | 2.5196 | 7.7513
0.174 | 367.9842 |  | 367.9842 | 150.9859 | 0.174 | 0.42388 | 2.4361 | 2.5222 | 7.7592
0.161 | 397.187 | mu ratio | 397.187 | 162.968 | 0.161 | 0.39272 | 2.4392 | 2.5255 | 7.7692
0.149 | 428.7072 | 0.82025 | 428.7072 | 175.9009 | 0.149 | 0.36384 | 2.4419 | 2.5282 | 7.7777
0.138 | 462.7289 |  | 462.7289 | 189.8602 | 0.138 | 0.33709 | 2.4427 | 2.529 | 7.7802
0.128 | 499.4505 | v ratio | 499.4505 | 204.9273 | 0.128 | 0.31231 | 2.4399 | 2.5261 | 7.7713
0.119 | 539.0863 | 3.0764 | 539.0863 | 221.1901 | 0.119 | 0.28934 | 2.4315 | 2.5174 | 7.7445
0.11 | 581.8675 |  | 581.8675 | 238.7434 | 0.11 | 0.26807 | 2.437 | 2.5232 | 7.7621
0.102 | 628.0438 | Re ratio | 628.0438 | 257.6898 | 0.102 | 0.255 | 2.5 | 2.5884 | 7.9628
0.094 | 677.8846 | 0.41031 | 677.8846 | 278.1398 | 0.094 | 0.236 | 2.5106 | 2.5994 | 7.9967
0.087 | 731.6807 |  | 731.6807 | 300.2126 | 0.087 | 0.219 | 2.5172 | 2.6062 | 8.0177
0.081 | 789.746 |  | 789.746 | 324.0371 | 0.081 | 0.203 | 2.5062 | 2.5948 | 7.9824
0.075 | 852.4193 |  | 852.4193 | 349.7523 | 0.075 | 0.188 | 2.5067 | 2.5953 | 7.984
0.07 | 920.0662 |  | 920.0662 | 377.5082 | 0.07 | 0.174 | 2.4857 | 2.5736 | 7.9173
0.064 | 993.0816 |  | 993.0816 | 407.4668 | 0.064 | 0.161 | 2.5156 | 2.6046 | 8.0125
0.06 | 1071.8913 |  | 1071.8913 | 439.8029 | 0.06 | 0.149 | 2.4833 | 2.5711 | 7.9097
0.055 | 1156.9553 |  | 1156.9553 | 474.7051 | 0.055 | 0.138 | 2.5091 | 2.5978 | 7.9917
0.051 | 1248.7699 |  | 1248.7699 | 512.3771 | 0.051 | 0.128 | 2.5098 | 2.5985 | 7.994
0.047 | 1347.8707 |  | 1347.8707 | 553.0387 | 0.047 | 0.119 | 2.5319 | 2.6214 | 8.0644
0.044 | 1454.8361 |  | 1454.8361 | 596.9272 | 0.044 | 0.11 | 2.5 | 2.5884 | 7.9628
0.041 | 1570.2901 |  | 1570.2901 | 644.2986 | 0.041 | 0.102 | 2.4878 | 2.5758 | 7.9239
0.038 | 1694.9064 |  | 1694.9064 | 695.4294 | 0.038 | 0.094 | 2.4737 | 2.5611 | 7.8789
0.035 | 1829.4121 |  | 1829.4121 | 750.6178 | 0.035 | 0.087 | 2.4857 | 2.5736 | 7.9173
0.033 | 1974.5921 |  | 1974.5921 | 810.1859 | 0.033 | 0.081 | 2.4545 | 2.5413 | 7.818
0.031 | 2131.2933 |  | 2131.2933 | 874.4813 | 0.031 | 0.075 | 2.4194 | 2.5049 | 7.7059
0.033 | 2300.4301 |  | 2300.4301 | 943.8791 | 0.033 | 0.07 | 2.1212 | 2.1962 | 6.7563
0.039 | 2482.9895 |  | 2482.9895 | 1018.7842 | 0.039 | 0.064 | 1.641 | 1.699 | 5.2268
0.043 | 2680.0365 |  | 2680.0365 | 1099.6336 | 0.043 | 0.06 | 1.3953 | 1.4447 | 4.4443
0.043 | 2892.7209 |  | 2892.7209 | 1186.8992 | 0.043 | 0.055 | 1.2791 | 1.3243 | 4.074
0.042 | 3122.2837 |  | 3122.2837 | 1281.0901 | 0.042 | 0.051 | 1.2143 | 1.2572 | 3.8676
0.041 | 3370.0643 |  | 3370.0643 | 1382.7558 | 0.041 | 0.047 | 1.1463 | 1.1869 | 3.6512
0.041 | 3637.5085 |  | 3637.5085 | 1492.4896 | 0.041 | 0.044 | 1.0732 | 1.1111 | 3.4182
0.04 | 3926.1768 |  | 3926.1768 | 1610.9318 | 0.04 | 0.041 | 1.025 | 1.0612 | 3.2647
0.039 | 4237.7534 |  | 4237.7534 | 1738.7734 | 0.039 | 0.038 | 0.97436 | 1.0088 | 3.1034
0.038 | 4574.0563 |  | 4574.0563 | 1876.7603 | 0.038 | 0.035 | 0.92105 | 0.95361 | 2.9337
0.037 | 4937.0479 |  | 4937.0479 | 2025.6978 | 0.037 | 0.033 | 0.89189 | 0.92342 | 2.8408
0.037 | 5328.846 |  | 5328.846 | 2186.4547 | 0.037 | 0.031 | 0.83784 | 0.86746 | 2.6686
0.036 | 5751.7367 |  | 5751.7367 | 2359.969 | 0.036 | 0.033 | 0.91667 | 0.94907 | 2.9197
0.035 | 6208.1875 |  | 6208.1875 | 2547.2533 | 0.035 | 0.039 | 1.1143 | 1.1537 | 3.5491
0.034 | 6700.8617 |  | 6700.8617 | 2749.4002 | 0.034 | 0.043 | 1.2647 | 1.3094 | 4.0282
0.034 | 7232.6339 |  | 7232.6339 | 2967.5892 | 0.034 | 0.043 | 1.2647 | 1.3094 | 4.0282
0.033 | 7806.6069 |  | 7806.6069 | 3203.0935 | 0.033 | 0.042 | 1.2727 | 1.3177 | 4.0538
0.032 | 8426.1297 |  | 8426.1297 | 3457.2871 | 0.032 | 0.041 | 1.2812 | 1.3265 | 4.0809
0.032 | 9094.8171 |  | 9094.8171 | 3731.6532 | 0.032 | 0.041 | 1.2812 | 1.3265 | 4.0809
0.031 | 9816.5707 |  | 9816.5707 | 4027.7926 | 0.031 | 0.04 | 1.2903 | 1.3359 | 4.1098
0.03 | 10595.6018 |  | 10595.6018 | 4347.4334 | 0.03 | 0.039 | 1.3 | 1.346 | 4.1406
0.03 | 11436.4558 |  | 11436.4558 | 4692.4404 | 0.03 | 0.038 | 1.2667 | 1.3114 | 4.0345
0.029 | 12344.039 |  | 12344.039 | 5064.8267 | 0.029 | 0.037 | 1.2759 | 1.321 | 4.0638
0.029 | 13323.6469 |  | 13323.6469 | 5466.7652 | 0.029 | 0.037 | 1.2759 | 1.321 | 4.0638
0.028 | 14380.9953 |  | 14380.9953 | 5900.601 | 0.028 | 0.036 | 1.2857 | 1.3312 | 4.0951
0.028 | 15522.2536 |  | 15522.2536 | 6368.8655 | 0.028 | 0.035 | 1.25 | 1.2942 | 3.9814
0.027 | 16754.0807 |  | 16754.0807 | 6874.2909 | 0.027 | 0.034 | 1.2593 | 1.3038 | 4.0109
0.027 | 18083.6641 |  | 18083.6641 | 7419.8263 | 0.027 | 0.034 | 1.2593 | 1.3038 | 4.0109
0.026 | 19518.7617 |  | 19518.7617 | 8008.6547 | 0.026 | 0.033 | 1.2692 | 1.3141 | 4.0426
0.026 | 21067.7468 |  | 21067.7468 | 8644.2117 | 0.026 | 0.032 | 1.2308 | 1.2743 | 3.9201
0.025 | 22739.6575 |  | 22739.6575 | 9330.2058 | 0.025 | 0.032 | 1.28 | 1.3253 | 4.0769
0.025 | 24544.249 |  | 24544.249 | 10070.6396 | 0.025 | 0.031 | 1.24 | 1.2838 | 3.9495
0.024 | 26492.0507 |  | 26492.0507 | 10869.8333 | 0.024 | 0.03 | 1.25 | 1.2942 | 3.9814
0.024 | 28594.4276 |  | 28594.4276 | 11732.45 | 0.024 | 0.03 | 1.25 | 1.2942 | 3.9814
0.023 | 30863.6465 |  | 30863.6465 | 12663.523 | 0.023 | 0.029 | 1.2609 | 1.3054 | 4.016
0.023 | 33312.9479 |  | 33312.9479 | 13668.4847 | 0.023 | 0.029 | 1.2609 | 1.3054 | 4.016
0.023 | 35956.6228 |  | 35956.6228 | 14753.199 | 0.023 | 0.028 | 1.2174 | 1.2604 | 3.8775
0.022 | 38810.0966 |  | 38810.0966 | 15923.9949 | 0.022 | 0.028 | 1.2727 | 1.3177 | 4.0538
0.022 | 41890.0186 |  | 41890.0186 | 17187.7037 | 0.022 | 0.027 | 1.2273 | 1.2707 | 3.909
0.021 | 45214.3594 |  | 45214.3594 | 18551.6989 | 0.021 | 0.027 | 1.2857 | 1.3312 | 4.0951
0.021 | 48802.5158 |  | 48802.5158 | 20023.9391 | 0.021 | 0.026 | 1.2381 | 1.2819 | 3.9435
0.021 | 52675.424 |  | 52675.424 | 21613.0145 | 0.021 | 0.026 | 1.2381 | 1.2819 | 3.9435
0.02 | 56855.6815 |  | 56855.6815 | 23328.197 | 0.02 | 0.025 | 1.25 | 1.2942 | 3.9814
0.02 | 61367.6791 |  | 61367.6791 | 25179.4943 | 0.02 | 0.025 | 1.25 | 1.2942 | 3.9814
0.02 | 66237.7433 |  | 66237.7433 | 27177.7083 | 0.02 | 0.024 | 1.2 | 1.2424 | 3.8221
0.019 | 71494.2899 |  | 71494.2899 | 29334.4981 | 0.019 | 0.024 | 1.2632 | 1.3078 | 4.0233
0.019 | 77167.9896 |  | 77167.9896 | 31662.4482 | 0.019 | 0.023 | 1.2105 | 1.2533 | 3.8557
0.019 | 83291.9472 |  | 83291.9472 | 34175.1415 | 0.019 | 0.023 | 1.2105 | 1.2533 | 3.8557
0.018 | 89901.8946 |  | 89901.8946 | 36887.239 | 0.018 | 0.023 | 1.2778 | 1.3229 | 4.0699
0.018 | 97036.3994 |  | 97036.3994 | 39814.5653 | 0.018 | 0.022 | 1.2222 | 1.2654 | 3.8929
0.018 | 104737.0898 |  | 104737.0898 | 42974.2007 | 0.018 | 0.022 | 1.2222 | 1.2654 | 3.8929
0.018 | 113048.8976 |  | 113048.8976 | 46384.5809 | 0.018 | 0.021 | 1.1667 | 1.2079 | 3.716
0.017 | 122020.3203 |  | 122020.3203 | 50065.6047 | 0.017 | 0.021 | 1.2353 | 1.279 | 3.9345
0.017 | 131703.7043 |  | 131703.7043 | 54038.7501 | 0.017 | 0.021 | 1.2353 | 1.279 | 3.9345
0.017 | 142155.5497 |  | 142155.5497 | 58327.1995 | 0.017 | 0.02 | 1.1765 | 1.2181 | 3.7472
0.016 | 153436.8409 |  | 153436.8409 | 62955.9749 | 0.016 | 0.02 | 1.25 | 1.2942 | 3.9814
0.016 | 165613.4016 |  | 165613.4016 | 67952.0844 | 0.016 | 0.02 | 1.25 | 1.2942 | 3.9814
0.016 | 178756.2793 |  | 178756.2793 | 73344.679 | 0.016 | 0.019 | 1.1875 | 1.2295 | 3.7823
0.016 | 192942.1598 |  | 192942.1598 | 79165.2233 | 0.016 | 0.019 | 1.1875 | 1.2295 | 3.7823
0.016 | 208253.8144 |  | 208253.8144 | 85447.679 | 0.016 | 0.019 | 1.1875 | 1.2295 | 3.7823
0.015 | 224780.5834 |  | 224780.5834 | 92228.7027 | 0.015 | 0.018 | 1.2 | 1.2424 | 3.8221
0.015 | 242618.8965 |  | 242618.8965 | 99547.8601 | 0.015 | 0.018 | 1.2 | 1.2424 | 3.8221
0.015 | 261872.8365 |  | 261872.8365 | 107447.857 | 0.015 | 0.018 | 1.2 | 1.2424 | 3.8221
0.015 | 282654.7456 |  | 282654.7456 | 115974.7879 | 0.015 | 0.018 | 1.2 | 1.2424 | 3.8221
0.014 | 305085.8817 |  | 305085.8817 | 125178.4057 | 0.014 | 0.017 | 1.2143 | 1.2572 | 3.8676
0.014 | 329297.1255 |  | 329297.1255 | 135112.4115 | 0.014 | 0.017 | 1.2143 | 1.2572 | 3.8676
0.014 | 355429.7441 |  | 355429.7441 | 145834.7678 | 0.014 | 0.017 | 1.2143 | 1.2572 | 3.8676
0.014 | 383636.2154 |  | 383636.2154 | 157408.0372 | 0.014 | 0.016 | 1.1429 | 1.1833 | 3.6401
0.014 | 414081.1179 |  | 414081.1179 | 169899.7472 | 0.014 | 0.016 | 1.1429 | 1.1833 | 3.6401
0.013 | 446942.0908 |  | 446942.0908 | 183382.7841 | 0.013 | 0.016 | 1.2308 | 1.2743 | 3.9201
0.013 | 482410.8704 |  | 482410.8704 | 197935.8183 | 0.013 | 0.016 | 1.2308 | 1.2743 | 3.9201
0.013 | 520694.4092 |  | 520694.4092 | 213643.7637 | 0.013 | 0.016 | 1.2308 | 1.2743 | 3.9201
0.013 | 562016.0829 |  | 562016.0829 | 230598.2724 | 0.013 | 0.015 | 1.1538 | 1.1946 | 3.6751
0.013 | 606616.9943 |  | 606616.9943 | 248898.2702 | 0.013 | 0.015 | 1.1538 | 1.1946 | 3.6751
0.013 | 654757.3797 |  | 654757.3797 | 268650.5336 | 0.013 | 0.015 | 1.1538 | 1.1946 | 3.6751
0.012 | 706718.1274 |  | 706718.1274 | 289970.3126 | 0.012 | 0.015 | 1.25 | 1.2942 | 3.9814
0.012 | 762802.4167 |  | 762802.4167 | 312982.0032 | 0.012 | 0.014 | 1.1667 | 1.2079 | 3.716
0.012 | 823337.4869 |  | 823337.4869 | 337819.8736 | 0.012 | 0.014 | 1.1667 | 1.2079 | 3.716
0.012 | 888676.5464 |  | 888676.5464 | 364628.847 | 0.012 | 0.014 | 1.1667 | 1.2079 | 3.716
0.012 | 959200.8341 |  | 959200.8341 | 393565.3479 | 0.012 | 0.014 | 1.1667 | 1.2079 | 3.716
0.012 | 1035321.8433 |  | 1035321.843 | 424798.2143 | 0.012 | 0.014 | 1.1667 | 1.2079 | 3.716
0.011 | 1117483.723 |  | 1117483.723 | 458509.6829 | 0.011 | 0.013 | 1.1818 | 1.2236 | 3.7642
0.011 | 1206165.8694 |  | 1206165.869 | 494896.4525 | 0.011 | 0.013 | 1.1818 | 1.2236 | 3.7642
0.011 | 1301885.7228 |  | 1301885.723 | 534170.8319 | 0.011 | 0.013 | 1.1818 | 1.2236 | 3.7642
0.011 | 1405201.7872 |  | 1405201.787 | 576561.9781 | 0.011 | 0.013 | 1.1818 | 1.2236 | 3.7642
0.011 | 1516716.8885 |  | 1516716.889 | 622317.234 | 0.011 | 0.013 | 1.1818 | 1.2236 | 3.7642
0.011 | 1637081.6923 |  | 1637081.692 | 671703.5713 | 0.011 | 0.013 | 1.1818 | 1.2236 | 3.7642
0.011 | 1766998.5003 |  | 1766998.5 | 725009.1481 | 0.011 | 0.012 | 1.0909 | 1.1295 | 3.4747
0.01 | 1907225.3478 |  | 1907225.348 | 782544.9905 | 0.01 | 0.012 | 1.2 | 1.2424 | 3.8221
0.01 | 2058580.4271 |  | 2058580.427 | 844646.8073 | 0.01 | 0.012 | 1.2 | 1.2424 | 3.8221
0.01 | 2221946.8609 |  | 2221946.861 | 911676.9485 | 0.01 | 0.012 | 1.2 | 1.2424 | 3.8221
0.01 | 2398277.8559 |  | 2398277.856 | 984026.52 | 0.01 | 0.012 | 1.2 | 1.2424 | 3.8221
0.01 | 2588602.2638 |  | 2588602.264 | 1062117.665 | 0.01 | 0.012 | 1.2 | 1.2424 | 3.8221
0.01 | 2794030.5847 |  | 2794030.585 | 1146406.029 | 0.01 | 0.011 | 1.1 | 1.1389 | 3.5036
0.01 | 3015761.4468 |  | 3015761.447 | 1237383.414 | 0.01 | 0.011 | 1.1 | 1.1389 | 3.5036
0.01 | 3255088.5998 |  | 3255088.6 | 1335580.654 | 0.01 | 0.011 | 1.1 | 1.1389 | 3.5036
0.009 | 3513408.4641 |  | 3513408.464 | 1441570.707 | 0.009 | 0.011 | 1.2222 | 1.2654 | 3.8929
0.009 | 3792228.278 |  | 3792228.278 | 1555972.001 | 0.009 | 0.011 | 1.2222 | 1.2654 | 3.8929
0.009 | 4093174.8925 |  | 4093174.893 | 1679452.043 | 0.009 | 0.011 | 1.2222 | 1.2654 | 3.8929
0.009 | 4418004.2636 |  | 4418004.264 | 1812731.311 | 0.009 | 0.011 | 1.2222 | 1.2654 | 3.8929
0.009 | 4768611.6977 |  | 4768611.698 | 1956587.458 | 0.009 | 0.01 | 1.1111 | 1.1504 | 3.539
0.009 | 5147042.9105 |  | 5147042.911 | 2111859.854 | 0.009 | 0.01 | 1.1111 | 1.1504 | 3.539
0.009 | 5555505.9631 |  | 5555505.963 | 2279454.479 | 0.009 | 0.01 | 1.1111 | 1.1504 | 3.539
0.009 | 5996384.1458 |  | 5996384.146 | 2460349.208 | 0.009 | 0.01 | 1.1111 | 1.1504 | 3.539
0.009 | 6472249.8838 |  | 6472249.884 | 2655599.523 | 0.009 | 0.01 | 1.1111 | 1.1504 | 3.539
0.009 | 6985879.7468 |  | 6985879.747 | 2866344.665 | 0.009 | 0.01 | 1.1111 | 1.1504 | 3.539
0.008 | 7540270.6497 |  | 7540270.65 | 3093814.284 | 0.008 | 0.01 | 1.25 | 1.2942 | 3.9814
0.008 | 8138657.3391 |  | 8138657.339 | 3339335.615 | 0.008 | 0.01 | 1.25 | 1.2942 | 3.9814
0.008 | 8784531.2669 |  | 8784531.267 | 3604341.22 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 9481660.9625 |  | 9481660.963 | 3890377.346 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 10234114.0211 |  | 10234114.02 | 4199112.951 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 11046280.8374 |  | 11046280.84 | 4532349.438 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 11922900.2224 |  | 11922900.22 | 4892031.166 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 12869087.0535 |  | 12869087.05 | 5280256.797 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 13890362.1184 |  | 13890362.12 | 5699291.541 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 14992684.3279 |  | 14992684.33 | 6151580.372 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 16182485.4844 |  | 16182485.48 | 6639762.293 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.008 | 17466707.8107 |  | 17466707.81 | 7166685.737 | 0.008 | 0.009 | 1.125 | 1.1648 | 3.5832
0.007 | 18852844.4558 |  | 18852844.46 | 7735425.183 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 20348983.2156 |  | 20348983.22 | 8349299.098 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 21963853.7242 |  | 21963853.72 | 9011889.3 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 23706878.3882 |  | 23706878.39 | 9727061.851 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 25588227.3653 |  | 25588227.37 | 10498989.63 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 27618877.9044 |  | 27618877.9 | 11332176.65 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 29810678.3956 |  | 29810678.4 | 12231484.38 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 32176417.5025 |  | 32176417.5 | 13202160.07 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 34729898.7818 |  | 34729898.78 | 14249867.4 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 37486021.2235 |  | 37486021.22 | 15380719.51 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 40460866.1833 |  | 40460866.18 | 16601314.67 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 43671791.2136 |  | 43671791.21 | 17918774.77 | 0.007 | 0.008 | 1.1429 | 1.1833 | 3.6401
0.007 | 47137531.3412 |  | 47137531.34 | 19340786.9 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 50878308.3815 |  | 50878308.38 | 20875648.17 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 54915948.9288 |  | 54915948.93 | 22532314.17 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 59274011.7093 |  | 59274011.71 | 24320451.16 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 63977925.0408 |  | 63977925.04 | 26250492.53 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 69055135.2016 |  | 69055135.2 | 28333699.62 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 74535266.5732 |  | 74535266.57 | 30582227.5 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 80450294.4916 |  | 80450294.49 | 33009195.8 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 86834731.8171 |  | 86834731.82 | 35628765.35 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 93725830.3078 |  | 93725830.31 | 38456220.75 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 101163797.9766 |  | 101163798 | 41508059.56 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.007 | 109192033.6949 |  | 109192033.7 | 44802088.58 | 0.007 | 0.007 | 1 | 1.0354 | 3.1851
0.008 | 117857380.4157 |  | 117857380.4 | 48357527.73 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 127210398.4917 |  | 127210398.5 | 52195122.19 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 137305660.6836 |  | 137305660.7 | 56337263.48 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 148202070.5799 |  | 148202070.6 | 60808120.05 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 159963206.286 |  | 159963206.3 | 65633778.35 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 172657691.3884 |  | 172657691.4 | 70842395.01 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 186359595.3576 |  | 186359595.4 | 76464361.14 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 201148865.7271 |  | 201148865.7 | 82532479.66 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 217111794.5695 |  | 217111794.6 | 89082156.66 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 234341521.9905 |  | 234341522 | 96151608.05 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 252938579.5817 |  | 252938579.6 | 103782082.5 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 273011476.999 |  | 273011477 | 112018102.1 | 0.008 | 0.007 | 0.875 | 0.90593 | 2.787
0.008 | 294677335.0922 |  | 294677335.1 | 120907722.1 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 318062569.2794 |  | 318062569.3 | 130502811.6 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 343303627.1519 |  | 343303627.2 | 140859355.7 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 370547784.6157 |  | 370547784.6 | 152037782.5 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 399954005.2131 |  | 399954005.2 | 164103315.6 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 431693867.6395 |  | 431693867.6 | 177126354.8 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 465952566.8665 |  | 465952566.9 | 191182886.4 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 502929994.7127 |  | 502929994.7 | 206354927.3 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 542841906.1681 |  | 542841906.2 | 222731002.8 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 585921178.2756 |  | 585921178.3 | 240406663.7 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 632419168.9166 |  | 632419168.9 | 259485043.6 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 682607183.4272 |  | 682607183.4 | 280077460.4 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 736778057.6049 |  | 736778057.6 | 302304066.3 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 795247866.3389 |  | 795247866.3 | 326294548.6 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 858357767.8363 |  | 858357767.8 | 352188886.4 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 926475994.204 |  | 926475994.2 | 380138167.2 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851
0.008 | 1000000000 |  | 1000000000 | 410305468.8 | 0.008 | 0.008 | 1 | 1.0354 | 3.1851

## chart
| NTSg | H2 | ratio
0 | 100.2% | 100.3% | 0.9987
5 | 99.8% | 99.98% | 0.99822
10 | 99.37% | 99.61% | 0.99759
15 | 98.88% | 99.2% | 0.99676
20 | 98.3% | 98.72% | 0.99567
25 | 97.62% | 98.18% | 0.99425
30 | 96.81% | 97.55% | 0.99239
35 | 95.82% | 96.8% | 0.98995
40 | 94.61% | 95.89% | 0.98674
45 | 93.11% | 94.77% | 0.98248
50 | 91.22% | 93.39% | 0.97679
51 | 90.78% | 93.07% | 0.97541
52 | 90.32% | 92.74% | 0.97397
53 | 89.84% | 92.39% | 0.97243
54 | 89.34% | 92.02% | 0.9708
55 | 88.8% | 91.64% | 0.96905
56 | 88.24% | 91.24% | 0.96719
56.3747 | 88.02% | 91.08% | 0.96645
57 | 88% | 90.81% | 0.969
58 | 87.96% | 90.36% | 0.97335
59 | 87.91% | 89.89% | 0.97801
60 | 87.87% | 89.39% | 0.983
61 | 87.83% | 88.87% | 0.98837
62 | 87.79% | 88.31% | 0.99414
63 | 87.75% | 87.72% | 1.0004
64 | 87.71% | 87.09% | 1.0071
65 | 87.67% | 86.43% | 1.0144
66 | 87.63% | 85.72% | 1.0223
67 | 87.59% | 84.97% | 1.0308
68 | 87.54% | 84.16% | 1.0402
69 | 87.5% | 83.3% | 1.0504
70 | 87.46% | 82.38% | 1.0617
70.0201 | 87.46% | 82.36% | 1.0619
71 | 87.42% | 82.33% | 1.0619
72 | 87.38% | 82.29% | 1.0618
73 | 87.34% | 82.26% | 1.0617
74 | 87.3% | 82.23% | 1.0617
75 | 87.26% | 82.19% | 1.0616
76 | 87.21% | 82.16% | 1.0616
77 | 87.17% | 82.12% | 1.0615
78 | 87.13% | 82.09% | 1.0615
79 | 87.09% | 82.05% | 1.0614
80 | 87.05% | 82.02% | 1.0613
81 | 87.01% | 81.98% | 1.0613
82 | 86.97% | 81.95% | 1.0612
83 | 86.93% | 81.92% | 1.0612
84 | 86.89% | 81.88% | 1.0611
85 | 86.84% | 81.85% | 1.061
86 | 86.8% | 81.81% | 1.061
87 | 86.76% | 81.78% | 1.0609
88 | 86.72% | 81.74% | 1.0609
89 | 86.68% | 81.71% | 1.0608
90 | 86.64% | 81.68% | 1.0608
91 | 86.6% | 81.64% | 1.0607
92 | 86.56% | 81.61% | 1.0606
93 | 86.51% | 81.57% | 1.0606
94 | 86.47% | 81.54% | 1.0605
95 | 86.43% | 81.5% | 1.0605
96 | 86.39% | 81.47% | 1.0604
97 | 86.35% | 81.44% | 1.0603
98 | 86.31% | 81.4% | 1.0603
99 | 86.27% | 81.37% | 1.0602
100 | 86.23% | 81.33% | 1.0602

## H2 overview
H2 reaction
1 H2 + 0.5 O2 -> H2O
|  | H2 | O2 | N2 | H2O (vap) | H2O (liq)
fuel | mol | 1
air |  |  | 0.575 | 2.1696 | 0
products | mol |  | 0.075 | 2.1696 | 1
product fraction | % |  | 2.312% | 66.87% | 30.82%
products | mol |  | 0.075 | 2.1696 | 0.31131 | 0.68869
product fraction | % |  | 2.934% | 84.89% | 12.18%
[5 empty] | condensed | 68.87%
HHV | kJ/mol | 285.826
Heat capacity | J/mol/K | 28.7557 | 29.3372 | 29.1181 | 32.8126 | 75.6328
heat of vaporiation | kJ/mol |  |  |  | 43.99
fuel inlet | C | 11
air inlet | C | 5
STP for combustion | C | 25
outlet temperature | C | 50 |  |  |  |  | subtotals
fuel sensible heat | kJ/mol | 0.40258 | 0 | 0 | 0 | 0 | 0.40258
air sensible heat | kJ/mol | 0 | 0.33738 | 1.2635 | 0 | 0 | 1.6009
outlet sensible heat | kJ/mol | 0 | 0.055007 | 1.5794 | 0.25538 | 1.3022 | 3.192 | 5.1954
latent heat | kJ/mol |  |  |  | 13.6947
total heat | kJ/mol(rxn) | 18.8901
Effective Heating Value | kJ/mol(rxn) | 266.9359 | 93.39%

## H2 plot
Outlet [C] | H2 | H2O mol vap | H2O mol liq | heat in sensible | O2 out sensible | N2 out sensible | H2O vap sensible | H2O liq sensible | H2O latent | total heat | Vapour Pressure | H2O mol vap
0 | 100.3% | 0.013549 | 0.98645 | 2.0035 | -0.055007 | -1.5794 | -0.011115 | -1.8652 | 0.59602 | -0.91122 | 0.006 | 0.013549 | 0
5 | 99.98% | 0.019471 | 0.98053 | 2.0035 | -0.044006 | -1.2635 | -0.012778 | -1.4832 | 0.85654 | 0.056514 | 0.0086 | 0.019471 | 0
10 | 99.61% | 0.027493 | 0.97251 | 2.0035 | -0.033004 | -0.94763 | -0.013532 | -1.1033 | 1.2094 | 1.1154 | 0.0121 | 0.027493 | 0
15 | 99.2% | 0.038354 | 0.96165 | 2.0035 | -0.022003 | -0.63176 | -0.012585 | -0.72732 | 1.6872 | 2.297 | 0.0168 | 0.038354 | 0
20 | 98.72% | 0.053077 | 0.94692 | 2.0035 | -0.011001 | -0.31588 | -0.008708 | -0.35809 | 2.3349 | 3.6446 | 0.0231 | 0.053077 | 0
25 | 98.18% | 0.072527 | 0.92747 | 2.0035 | 0 | 0 | 0 | 0 | 3.1905 | 5.1939 | 0.0313 | 0.072527 | 0
30 | 97.55% | 0.098163 | 0.90184 | 2.0035 | 0.011001 | 0.31588 | 0.016105 | 0.34104 | 4.3182 | 7.0057 | 0.0419 | 0.098163 | 0
35 | 96.8% | 0.1319 | 0.8681 | 2.0035 | 0.022003 | 0.63176 | 0.043279 | 0.65657 | 5.8022 | 9.1592 | 0.0555 | 0.1319 | 0
40 | 95.89% | 0.17624 | 0.82376 | 2.0035 | 0.033004 | 0.94763 | 0.086743 | 0.93455 | 7.7528 | 11.7582 | 0.0728 | 0.17624 | 0
45 | 94.77% | 0.23453 | 0.76547 | 2.0035 | 0.044006 | 1.2635 | 0.15391 | 1.1579 | 10.3169 | 14.9397 | 0.0946 | 0.23453 | 0
50 | 93.39% | 0.31131 | 0.68869 | 2.0035 | 0.055007 | 1.5794 | 0.25538 | 1.3022 | 13.6947 | 18.8901 | 0.1218 | 0.31131 | 0
51 | 93.07% | 0.32973 | 0.67027 | 2.0035 | 0.057208 | 1.6426 | 0.28131 | 1.318 | 14.505 | 19.8076 | 0.12808 | 0.32973 | 0
52 | 92.74% | 0.34891 | 0.65109 | 2.0035 | 0.059408 | 1.7057 | 0.30911 | 1.3296 | 15.3484 | 20.7557 | 0.13453 | 0.34891 | 0
53 | 92.39% | 0.36921 | 0.63079 | 2.0035 | 0.061608 | 1.7689 | 0.33921 | 1.3358 | 16.2414 | 21.7505 | 0.14125 | 0.36921 | 0
54 | 92.02% | 0.39071 | 0.60929 | 2.0035 | 0.063808 | 1.8321 | 0.37179 | 1.3364 | 17.1873 | 22.7949 | 0.14826 | 0.39071 | 0
55 | 91.64% | 0.4135 | 0.5865 | 2.0035 | 0.066009 | 1.8953 | 0.40704 | 1.3308 | 18.1898 | 23.8923 | 0.15556 | 0.4135 | 0
56 | 91.24% | 0.43766 | 0.56234 | 2.0035 | 0.068209 | 1.9584 | 0.44519 | 1.3185 | 19.2527 | 25.0465 | 0.16317 | 0.43766 | 0
56.3747 | 91.08% | 0.44721 | 0.55279 | 2.0035 | 0.069034 | 1.9821 | 0.4604 | 1.3117 | 19.6728 | 25.4996 | 0.16614 | 0.44721 | 0
57 | 90.81% | 0.4633 | 0.5367 | 2.0035 | 0.070409 | 2.0216 | 0.48646 | 1.299 | 20.3804 | 26.2613 | 0.17109 | 0.4633 | 0
58 | 90.36% | 0.49052 | 0.50948 | 2.0035 | 0.07261 | 2.0848 | 0.53114 | 1.2716 | 21.5778 | 27.5414 | 0.17934 | 0.49052 | 0
59 | 89.89% | 0.51943 | 0.48057 | 2.0035 | 0.07481 | 2.148 | 0.57949 | 1.2358 | 22.8498 | 28.8913 | 0.18792 | 0.51943 | 0
60 | 89.39% | 0.55017 | 0.44983 | 2.0035 | 0.07701 | 2.2111 | 0.63184 | 1.1908 | 24.2022 | 30.3164 | 0.19686 | 0.55017 | 0
61 | 88.87% | 0.58289 | 0.41711 | 2.0035 | 0.07921 | 2.2743 | 0.68854 | 1.1357 | 25.6412 | 31.8224 | 0.20615 | 0.58289 | 0
62 | 88.31% | 0.61772 | 0.38228 | 2.0035 | 0.081411 | 2.3375 | 0.74996 | 1.0698 | 27.1737 | 33.4158 | 0.21581 | 0.61772 | 0
63 | 87.72% | 0.65487 | 0.34513 | 2.0035 | 0.083611 | 2.4007 | 0.81654 | 0.99193 | 28.8075 | 35.1038 | 0.22586 | 0.65487 | 0
64 | 87.09% | 0.6945 | 0.3055 | 2.0035 | 0.085811 | 2.4638 | 0.88875 | 0.90112 | 30.5512 | 36.8942 | 0.2363 | 0.6945 | 0
65 | 86.43% | 0.73684 | 0.26316 | 2.0035 | 0.088012 | 2.527 | 0.96711 | 0.79613 | 32.4138 | 38.7955 | 0.24714 | 0.73684 | 0
66 | 85.72% | 0.78214 | 0.21786 | 2.0035 | 0.090212 | 2.5902 | 1.0522 | 0.67558 | 34.4063 | 40.8179 | 0.25841 | 0.78214 | 0
67 | 84.97% | 0.83065 | 0.16935 | 2.0035 | 0.092412 | 2.6534 | 1.1447 | 0.53795 | 36.5404 | 42.9723 | 0.27011 | 0.83065 | 0
68 | 84.16% | 0.88268 | 0.11732 | 2.0035 | 0.094613 | 2.7165 | 1.2454 | 0.38153 | 38.8293 | 45.2709 | 0.28225 | 0.88268 | 0
69 | 83.3% | 0.93858 | 0.061421 | 2.0035 | 0.096813 | 2.7797 | 1.3551 | 0.2044 | 41.2881 | 47.7276 | 0.29485 | 0.93858 | 0
70 | 82.38% | 0.99872 | 0.0012778 | 2.0035 | 0.099013 | 2.8429 | 1.4747 | 0.0043489 | 43.9338 | 50.3582 | 0.30793 | 0.99872 | 0
70.0201 | 82.36% | 1 | 0 | 2.0035 | 0.099057 | 2.8442 | 1.4772 | 0 | 43.99 | 50.4139 | 0.3082 | 1 | 0
71 | 82.33% | 1 | 0 | 2.0035 | 0.10121 | 2.9061 | 1.5094 | 0 | 43.99 | 50.5101 | 0.32149 | 1 | 0
72 | 82.29% | 1 | 0 | 2.0035 | 0.10341 | 2.9693 | 1.5422 | 0 | 43.99 | 50.6083 | 0.33556 | 1 | 0
73 | 82.26% | 1 | 0 | 2.0035 | 0.10561 | 3.0324 | 1.575 | 0 | 43.99 | 50.7065 | 0.35014 | 1 | 0
74 | 82.23% | 1 | 0 | 2.0035 | 0.10781 | 3.0956 | 1.6078 | 0 | 43.99 | 50.8047 | 0.36525 | 1 | 0
75 | 82.19% | 1 | 0 | 2.0035 | 0.11001 | 3.1588 | 1.6406 | 0 | 43.99 | 50.9029 | 0.38091 | 1 | 0
76 | 82.16% | 1 | 0 | 2.0035 | 0.11221 | 3.222 | 1.6734 | 0 | 43.99 | 51.0011 | 0.39713 | 1 | 0
77 | 82.12% | 1 | 0 | 2.0035 | 0.11442 | 3.2851 | 1.7063 | 0 | 43.99 | 51.0993 | 0.41392 | 1 | 0
78 | 82.09% | 1 | 0 | 2.0035 | 0.11662 | 3.3483 | 1.7391 | 0 | 43.99 | 51.1975 | 0.43132 | 1 | 0
79 | 82.05% | 1 | 0 | 2.0035 | 0.11882 | 3.4115 | 1.7719 | 0 | 43.99 | 51.2956 | 0.44932 | 1 | 0
80 | 82.02% | 1 | 0 | 2.0035 | 0.12102 | 3.4747 | 1.8047 | 0 | 43.99 | 51.3938 | 0.46794 | 1 | 0
81 | 81.98% | 1 | 0 | 2.0035 | 0.12322 | 3.5378 | 1.8375 | 0 | 43.99 | 51.492 | 0.48722 | 1 | 0
82 | 81.95% | 1 | 0 | 2.0035 | 0.12542 | 3.601 | 1.8703 | 0 | 43.99 | 51.5902 | 0.50715 | 1 | 0
83 | 81.92% | 1 | 0 | 2.0035 | 0.12762 | 3.6642 | 1.9031 | 0 | 43.99 | 51.6884 | 0.52777 | 1 | 0
84 | 81.88% | 1 | 0 | 2.0035 | 0.12982 | 3.7274 | 1.9359 | 0 | 43.99 | 51.7866 | 0.54908 | 1 | 0
85 | 81.85% | 1 | 0 | 2.0035 | 0.13202 | 3.7905 | 1.9688 | 0 | 43.99 | 51.8848 | 0.5711 | 1 | 0
86 | 81.81% | 1 | 0 | 2.0035 | 0.13422 | 3.8537 | 2.0016 | 0 | 43.99 | 51.983 | 0.59386 | 1 | 0
87 | 81.78% | 1 | 0 | 2.0035 | 0.13642 | 3.9169 | 2.0344 | 0 | 43.99 | 52.0812 | 0.61738 | 1 | 0
88 | 81.74% | 1 | 0 | 2.0035 | 0.13862 | 3.9801 | 2.0672 | 0 | 43.99 | 52.1793 | 0.64167 | 1 | 0
89 | 81.71% | 1 | 0 | 2.0035 | 0.14082 | 4.0432 | 2.1 | 0 | 43.99 | 52.2775 | 0.66675 | 1 | 0
90 | 81.68% | 1 | 0 | 2.0035 | 0.14302 | 4.1064 | 2.1328 | 0 | 43.99 | 52.3757 | 0.69264 | 1 | 0
91 | 81.64% | 1 | 0 | 2.0035 | 0.14522 | 4.1696 | 2.1656 | 0 | 43.99 | 52.4739 | 0.71937 | 1 | 0
92 | 81.61% | 1 | 0 | 2.0035 | 0.14742 | 4.2328 | 2.1984 | 0 | 43.99 | 52.5721 | 0.74695 | 1 | 0
93 | 81.57% | 1 | 0 | 2.0035 | 0.14962 | 4.2959 | 2.2313 | 0 | 43.99 | 52.6703 | 0.7754 | 1 | 0
94 | 81.54% | 1 | 0 | 2.0035 | 0.15182 | 4.3591 | 2.2641 | 0 | 43.99 | 52.7685 | 0.80475 | 1 | 0
95 | 81.5% | 1 | 0 | 2.0035 | 0.15402 | 4.4223 | 2.2969 | 0 | 43.99 | 52.8667 | 0.83502 | 1 | 0
96 | 81.47% | 1 | 0 | 2.0035 | 0.15622 | 4.4855 | 2.3297 | 0 | 43.99 | 52.9649 | 0.86623 | 1 | 0
97 | 81.44% | 1 | 0 | 2.0035 | 0.15842 | 4.5486 | 2.3625 | 0 | 43.99 | 53.063 | 0.8984 | 1 | 0
98 | 81.4% | 1 | 0 | 2.0035 | 0.16062 | 4.6118 | 2.3953 | 0 | 43.99 | 53.1612 | 0.93156 | 1 | 0
99 | 81.37% | 1 | 0 | 2.0035 | 0.16282 | 4.675 | 2.4281 | 0 | 43.99 | 53.2594 | 0.96572 | 1 | 0
100 | 81.33% | 1 | 0 | 2.0035 | 0.16502 | 4.7382 | 2.4609 | 0 | 43.99 | 53.3576 | 1 | #DIV/0! | 0

## NTSg overview
NTSg reaction
1 C1.119H4.239 + 2.179 O2 -> 1.119 CO2 + 2.119 H2O
|  | C1.119H4.239 | O2 | N2 | CO2 | H2O (vap) | H2O (liq)
fuel | mol | 0.9699 |  | 0.009354 | 0.020743
air |  |  | 2.4306 | 9.1712 |  | 0
products | mol |  | 0.31703 | 9.1805 | 1.1402 | 2.1194
product fraction | % |  | 2.485% | 71.96% | 8.937% | 16.61%
products | mol |  | 0.31703 | 9.1805 | 1.1402 | 1.7693 | 0.35009
product fraction | % |  | 2.555% | 73.99% | 9.19% | 12.18%
[6 empty] | condensed | 16.52%
HHV | kJ/mol | 940.8132
Heat capacity | J/mol/K | 37.376 | 29.3372 | 29.1181 | 36.2775 | 32.8126 | 75.6328
heat of vaporiation | kJ/mol |  |  |  |  | 43.99
fuel inlet | C | 11
air inlet | C | 5
STP | C | 25
outlet temperature | C | 50 | [5 empty] | subtotals
fuel sensible heat | kJ/mol | 0.50752 | 0 | 0.0038132 | 0.010535 | 0 | 0 | 0.52186
air sensible heat | kJ/mol | 0 | 1.4261 | 5.3409 | 0 | 0 | 0 | 6.7671
outlet sensible heat | kJ/mol | 0 | 0.23252 | 6.683 | 1.034 | 1.4514 | 0.66196 | 9.4009
latent heat | kJ/mol |  |  |  |  | 77.8323
total heat | kJ/mol(rxn) | 94.5222
Effective Heating Value | kJ/mol(rxn) | 846.291 | 89.95%

## NTSg plot
Outlet [C] | NTSg | H2O mol vap | H2O mol liq | heat in sensible | O2 out sensible | N2 out sensible | CO2 out sensible | H2O vap sensible | H2O liq sensible | H2O latent | total heat
0 | 100.2% | 0.064211 | 2.0552 | 7.2889 | -0.23252 | -6.683 | -1.034 | -0.052674 | -3.886 | 2.8247 | -1.7746
5 | 99.8% | 0.092278 | 2.0271 | 7.2889 | -0.18602 | -5.3464 | -0.82724 | -0.060558 | -3.0664 | 4.0593 | 1.8617
10 | 99.37% | 0.13029 | 1.9891 | 7.2889 | -0.13951 | -4.0098 | -0.62043 | -0.064129 | -2.2566 | 5.7316 | 5.93
15 | 98.88% | 0.18177 | 1.9376 | 7.2889 | -0.093008 | -2.6732 | -0.41362 | -0.059643 | -1.4655 | 7.9959 | 10.5799
20 | 98.3% | 0.25154 | 1.8679 | 7.2889 | -0.046504 | -1.3366 | -0.20681 | -0.041269 | -0.70636 | 11.0653 | 16.0167
25 | 97.62% | 0.34372 | 1.7757 | 7.2889 | 0 | 0 | 0 | 0 | 0 | 15.1202 | 22.4091
30 | 96.81% | 0.46521 | 1.6542 | 7.2889 | 0.046504 | 1.3366 | 0.20681 | 0.076324 | 0.62556 | 20.4647 | 30.0454
35 | 95.82% | 0.62508 | 1.4943 | 7.2889 | 0.093008 | 2.6732 | 0.41362 | 0.20511 | 1.1302 | 27.4975 | 39.3015
40 | 94.61% | 0.83523 | 1.2842 | 7.2889 | 0.13951 | 4.0098 | 0.62043 | 0.41109 | 1.4569 | 36.7417 | 50.6683
45 | 93.11% | 1.1115 | 1.0079 | 7.2889 | 0.18602 | 5.3464 | 0.82724 | 0.72941 | 1.5247 | 48.8936 | 64.7962
50 | 91.22% | 1.4754 | 0.64404 | 7.2889 | 0.23252 | 6.683 | 1.034 | 1.2103 | 1.2178 | 64.9016 | 82.5681
51 | 90.78% | 1.5627 | 0.55674 | 7.2889 | 0.24182 | 6.9503 | 1.0754 | 1.3332 | 1.0948 | 68.7419 | 86.7263
52 | 90.32% | 1.6535 | 0.46588 | 7.2889 | 0.25112 | 7.2176 | 1.1168 | 1.4649 | 0.95138 | 72.7386 | 91.0293
53 | 89.84% | 1.7497 | 0.36967 | 7.2889 | 0.26042 | 7.4849 | 1.1581 | 1.6076 | 0.78286 | 76.9709 | 95.5538
54 | 89.34% | 1.8516 | 0.26777 | 7.2889 | 0.26972 | 7.7523 | 1.1995 | 1.762 | 0.5873 | 81.4538 | 100.3135
55 | 88.8% | 1.9596 | 0.15977 | 7.2889 | 0.27902 | 8.0196 | 1.2409 | 1.929 | 0.36251 | 86.2046 | 105.3245
56 | 88.24% | 2.0742 | 0.045256 | 7.2889 | 0.28832 | 8.2869 | 1.2822 | 2.1098 | 0.10611 | 91.242 | 110.6043
56.3747 | 88.02% | 2.1194 | 0 | 7.2889 | 0.29181 | 8.3871 | 1.2977 | 2.1819 | 0 | 93.2328 | 112.6803
57 | 88% | 2.1194 | 0 | 7.2889 | 0.29762 | 8.5542 | 1.3236 | 2.2254 | 0 | 93.2328 | 112.9226
58 | 87.96% | 2.1194 | 0 | 7.2889 | 0.30693 | 8.8215 | 1.3649 | 2.2949 | 0 | 93.2328 | 113.3101
59 | 87.91% | 2.1194 | 0 | 7.2889 | 0.31623 | 9.0889 | 1.4063 | 2.3645 | 0 | 93.2328 | 113.6976
60 | 87.87% | 2.1194 | 0 | 7.2889 | 0.32553 | 9.3562 | 1.4477 | 2.434 | 0 | 93.2328 | 114.0851
61 | 87.83% | 2.1194 | 0 | 7.2889 | 0.33483 | 9.6235 | 1.489 | 2.5036 | 0 | 93.2328 | 114.4727
62 | 87.79% | 2.1194 | 0 | 7.2889 | 0.34413 | 9.8908 | 1.5304 | 2.5731 | 0 | 93.2328 | 114.8602
63 | 87.75% | 2.1194 | 0 | 7.2889 | 0.35343 | 10.1581 | 1.5718 | 2.6427 | 0 | 93.2328 | 115.2477
64 | 87.71% | 2.1194 | 0 | 7.2889 | 0.36273 | 10.4254 | 1.6131 | 2.7122 | 0 | 93.2328 | 115.6352
65 | 87.67% | 2.1194 | 0 | 7.2889 | 0.37203 | 10.6928 | 1.6545 | 2.7817 | 0 | 93.2328 | 116.0228
66 | 87.63% | 2.1194 | 0 | 7.2889 | 0.38133 | 10.9601 | 1.6958 | 2.8513 | 0 | 93.2328 | 116.4103
67 | 87.59% | 2.1194 | 0 | 7.2889 | 0.39063 | 11.2274 | 1.7372 | 2.9208 | 0 | 93.2328 | 116.7978
68 | 87.54% | 2.1194 | 0 | 7.2889 | 0.39993 | 11.4947 | 1.7786 | 2.9904 | 0 | 93.2328 | 117.1853
69 | 87.5% | 2.1194 | 0 | 7.2889 | 0.40923 | 11.762 | 1.8199 | 3.0599 | 0 | 93.2328 | 117.5729
70 | 87.46% | 2.1194 | 0 | 7.2889 | 0.41853 | 12.0294 | 1.8613 | 3.1295 | 0 | 93.2328 | 117.9604
70.0201 | 87.46% | 2.1194 | 0 | 7.2889 | 0.41872 | 12.0347 | 1.8621 | 3.1309 | 0 | 93.2328 | 117.9682
71 | 87.42% | 2.1194 | 0 | 7.2889 | 0.42784 | 12.2967 | 1.9026 | 3.199 | 0 | 93.2328 | 118.3479
72 | 87.38% | 2.1194 | 0 | 7.2889 | 0.43714 | 12.564 | 1.944 | 3.2685 | 0 | 93.2328 | 118.7354
73 | 87.34% | 2.1194 | 0 | 7.2889 | 0.44644 | 12.8313 | 1.9854 | 3.3381 | 0 | 93.2328 | 119.123
74 | 87.3% | 2.1194 | 0 | 7.2889 | 0.45574 | 13.0986 | 2.0267 | 3.4076 | 0 | 93.2328 | 119.5105
75 | 87.26% | 2.1194 | 0 | 7.2889 | 0.46504 | 13.366 | 2.0681 | 3.4772 | 0 | 93.2328 | 119.898
76 | 87.21% | 2.1194 | 0 | 7.2889 | 0.47434 | 13.6333 | 2.1095 | 3.5467 | 0 | 93.2328 | 120.2855
77 | 87.17% | 2.1194 | 0 | 7.2889 | 0.48364 | 13.9006 | 2.1508 | 3.6163 | 0 | 93.2328 | 120.6731
78 | 87.13% | 2.1194 | 0 | 7.2889 | 0.49294 | 14.1679 | 2.1922 | 3.6858 | 0 | 93.2328 | 121.0606
79 | 87.09% | 2.1194 | 0 | 7.2889 | 0.50224 | 14.4352 | 2.2335 | 3.7553 | 0 | 93.2328 | 121.4481
80 | 87.05% | 2.1194 | 0 | 7.2889 | 0.51154 | 14.7026 | 2.2749 | 3.8249 | 0 | 93.2328 | 121.8356
81 | 87.01% | 2.1194 | 0 | 7.2889 | 0.52084 | 14.9699 | 2.3163 | 3.8944 | 0 | 93.2328 | 122.2232
82 | 86.97% | 2.1194 | 0 | 7.2889 | 0.53014 | 15.2372 | 2.3576 | 3.964 | 0 | 93.2328 | 122.6107
83 | 86.93% | 2.1194 | 0 | 7.2889 | 0.53944 | 15.5045 | 2.399 | 4.0335 | 0 | 93.2328 | 122.9982
84 | 86.89% | 2.1194 | 0 | 7.2889 | 0.54875 | 15.7718 | 2.4404 | 4.1031 | 0 | 93.2328 | 123.3857
85 | 86.84% | 2.1194 | 0 | 7.2889 | 0.55805 | 16.0391 | 2.4817 | 4.1726 | 0 | 93.2328 | 123.7733
86 | 86.8% | 2.1194 | 0 | 7.2889 | 0.56735 | 16.3065 | 2.5231 | 4.2422 | 0 | 93.2328 | 124.1608
87 | 86.76% | 2.1194 | 0 | 7.2889 | 0.57665 | 16.5738 | 2.5644 | 4.3117 | 0 | 93.2328 | 124.5483
88 | 86.72% | 2.1194 | 0 | 7.2889 | 0.58595 | 16.8411 | 2.6058 | 4.3812 | 0 | 93.2328 | 124.9359
89 | 86.68% | 2.1194 | 0 | 7.2889 | 0.59525 | 17.1084 | 2.6472 | 4.4508 | 0 | 93.2328 | 125.3234
90 | 86.64% | 2.1194 | 0 | 7.2889 | 0.60455 | 17.3757 | 2.6885 | 4.5203 | 0 | 93.2328 | 125.7109
91 | 86.6% | 2.1194 | 0 | 7.2889 | 0.61385 | 17.6431 | 2.7299 | 4.5899 | 0 | 93.2328 | 126.0984
92 | 86.56% | 2.1194 | 0 | 7.2889 | 0.62315 | 17.9104 | 2.7712 | 4.6594 | 0 | 93.2328 | 126.486
93 | 86.51% | 2.1194 | 0 | 7.2889 | 0.63245 | 18.1777 | 2.8126 | 4.729 | 0 | 93.2328 | 126.8735
94 | 86.47% | 2.1194 | 0 | 7.2889 | 0.64175 | 18.445 | 2.854 | 4.7985 | 0 | 93.2328 | 127.261
95 | 86.43% | 2.1194 | 0 | 7.2889 | 0.65105 | 18.7123 | 2.8953 | 4.868 | 0 | 93.2328 | 127.6485
96 | 86.39% | 2.1194 | 0 | 7.2889 | 0.66035 | 18.9797 | 2.9367 | 4.9376 | 0 | 93.2328 | 128.0361
97 | 86.35% | 2.1194 | 0 | 7.2889 | 0.66966 | 19.247 | 2.9781 | 5.0071 | 0 | 93.2328 | 128.4236
98 | 86.31% | 2.1194 | 0 | 7.2889 | 0.67896 | 19.5143 | 3.0194 | 5.0767 | 0 | 93.2328 | 128.8111
99 | 86.27% | 2.1194 | 0 | 7.2889 | 0.68826 | 19.7816 | 3.0608 | 5.1462 | 0 | 93.2328 | 129.1986
100 | 86.23% | 2.1194 | 0 | 7.2889 | 0.69756 | 20.0489 | 3.1021 | 5.2158 | 0 | 93.2328 | 129.5862

## Biogas overview
biogas reaction
0.68 CH4 + 1.36 O2 -> 0.68 CO2 + 1.36 H2O
|  | CH4 | O2 | N2 | CO2 | H2O (vap) | H2O (liq)
fuel | mol | 0.68 |  |  | 0.26 | 0.06
air |  |  | 1.564 | 5.9014 |  | 0
products | mol |  | 0.082202 | 5.9014 | 0.94 | 1.42
product fraction | % |  | 0.9852% | 70.73% | 11.27% | 17.02%
products | mol |  | 0.082202 | 5.9014 | 0.94 | 1.1572 | 0.2628
product fraction | % |  | 1.017% | 73.03% | 11.63% | 12.18%
[6 empty] | condensed | 18.51%
HHV | kJ/mol | 605.6094
Heat capacity | J/mol/K | 37.376 | 29.3372 | 29.1181 | 36.2775 | 32.8126 | 75.6328
heat of vaporiation | kJ/mol |  |  |  |  | 43.99
fuel inlet | C | 11
air inlet | C | 5
STP | C | 25
outlet temperature | C | 50 | [5 empty] | subtotals
fuel sensible heat | kJ/mol | 0.35582 | 0 | 0 | 0.13205 | 0.027563 | 0 | 0.51543
air sensible heat | kJ/mol | 0 | 0.91767 | 3.4367 | 0 | 0 | 0 | 4.3544
outlet sensible heat | kJ/mol | 0 | 0.060289 | 4.2959 | 0.85252 | 0.94927 | 0.49691 | 6.158
latent heat | kJ/mol |  |  |  |  | 50.9051
total heat | kJ/mol(rxn) | 61.9329
Effective Heating Value | kJ/mol(rxn) | 543.6764 | 89.77%

## CH4 overview
biogas reaction
0.68 CH4 + 1.36 O2 -> 0.68 CO2 + 1.36 H2O
|  | CH4 | O2 | N2 | CO2 | H2O (vap) | H2O (liq)
fuel | mol | 1 |  |  | 0
air |  |  | 2.3 | 8.6785 |  | 0
products | mol |  | 0.12089 | 8.6785 | 1 | 2
product fraction | % |  | 1.025% | 73.55% | 8.475% | 16.95%
products | mol |  | 0.12089 | 8.6785 | 1 | 1.6365 | 0.36351
product fraction | % |  | 1.057% | 75.89% | 8.744% | 12.18%
[6 empty] | condensed | 18.18%
HHV | kJ/mol | 890.602
Heat capacity | J/mol/K | 37.376 | 29.3372 | 29.1181 | 36.2775 | 32.8126 | 75.6328
heat of vaporiation | kJ/mol |  |  |  |  | 43.99
fuel inlet | C | 11
air inlet | C | 5
STP | C | 25
outlet temperature | C | 50 | [5 empty] | subtotals
fuel sensible heat | kJ/mol | 0.52326 | 0 | 0 | 0 | 0 | 0 | 0.52326
air sensible heat | kJ/mol | 0 | 1.3495 | 5.054 | 0 | 0 | 0 | 6.4036
outlet sensible heat | kJ/mol | 0 | 0.088661 | 6.3176 | 0.90694 | 1.3424 | 0.68733 | 8.6556
latent heat | kJ/mol |  |  |  |  | 71.9893
total heat | kJ/mol(rxn) | 87.5717
Effective Heating Value | kJ/mol(rxn) | 803.0303 | 90.17%